## Criteria (hidden)
MenuSheetLink | 1 | MenuSheetLink1 | 1
| Data Entry |  | Charts
| Main Menu |  | Main Menu
| Filters 1 - 6 |  | Charts 1 - 4
| Filters 7 - 12 |  | Charts 5 - 8
Charts 9 - 12

## Summary
Plant Name | Rocky Mountain Water District
Plant PWS # | 1031099
Filter Description | All filters with filter-to-waste capability
Summary Table of Filter Return to Service Performance
|  | Maximum | Maximum | RTS | RTS | FTW
Filter | Description | Turbidity (NTU) | Turbidity (NTU) | Turbidity (NTU) | Turbidity (NTU) | Time (min)
|  | 95th Percentile | % Values < Goal | 95th Percentile | % Values < Goal | Average
1 | 0 | 0.3142 | 94.2857 | 0.161 | 68.8679 | 25.2642
2 | 0 | 0.2746 | 95.9596 | 0.1844 | 77.7778 | 24.8283
3 | 0 | 0.3308 | 92.3077 | 0.15935 | 75.9615 | 24.0288
4 | 0 | 0.3142 | 94.2857 | 0.161 | 68.8679 | 25.2642
5 | 0 | 0.2746 | 95.9596 | 0.1844 | 77.7778 | 24.8283
6 | 0 | 0.3308 | 92.3077 | 0.15935 | 75.9615 | 24.0288
7 | 0 | 0.3142 | 94.2857 | 0.161 | 68.8679 | 25.2642
8 | 0 | 0.2746 | 95.9596 | 0.1844 | 77.7778 | 24.8283
9 | 0 | 0.3308 | 92.3077 | 0.15935 | 75.9615 | 24.0288
10 | 0 | 0.3142 | 94.2857 | 0.161 | 68.8679 | 25.2642
11 | 0 | 0.3308 | 95.9596 | 0.1844 | 77.7778 | 24.8283
12 | 0 | 0.3308 | 92.3077 | 0.15935 | 75.9615 | 24.0288
Note on D10: Plants with filter-to-waste (FTW) capability: Maximum turbidity during FTW period. Plants without FTW capability: Maximum turbidity during 15 minutes following return to service.
Note on E10: Plants with filter-to-waste (FTW) capability: Maximum turbidity during FTW period. Plants without FTW capability: Maximum turbidity during 15 minutes following return to service.
Note on F6: Include whether filters have filter-to-waste capability or not.
Note on F10: Plants with Filter-to-waste (FTW) capability: Turbidity before filter is returned to service (RTS). Plants without FTW capability: Turbidity 15 minutes after filter is returned to service.
Note on G10: Plants with Filter-to-waste (FTW) capability: Turbidity before filter is returned to service (RTS). Plants without FTW capability: Turbidity 15 minutes after filter is returned to service.
Note on H10: Plants with filter-to-waste (FTW) capability: FTW time in minutes.

## Filters1-6BWData (hidden)
Data input screen for filter backwash data.
For filters with filter-to-waste (FTW) capability, input three values per backwash: 1) max. turbidity during FTW period,
2) turbidity at end of FTW period and 3) FTW time.
For filters without FTW capability, input two values per backwash: 1) max. turbidity during initial 15 minutes of filter run
and 2) turbidity after 15 minutes of filter run.
Filter | 1 |  |  | 2 |  |  | 3 |  |  | 4 |  |  | 5 |  |  | 6
Discription
Perf. Goals (NTU) | 0.3 | 0.1 |  | 0.3 | 0.1 |  | 0.3 | 0.1 |  | 0.3 | 0.1 |  | 0.3 | 0.1 |  | 0.3 | 0.1
% values < Goal | 94.2857 | 68.8679 |  | 95.9596 | 77.7778 |  | 92.3077 | 75.9615 |  | 94.2857 | 68.8679 |  | 95.9596 | 77.7778 |  | 92.3077 | 75.9615
95th % NTU | 0.3142 | 0.161 |  | 0.2746 | 0.1844 |  | 0.3308 | 0.15935 |  | 0.3142 | 0.161 |  | 0.2746 | 0.1844 |  | 0.3308 | 0.15935
| Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min)
2008-01-01 | [6 empty] | 0.101 | 0.059 | 15 | [6 empty] | 0.101 | 0.059 | 15 | 0.1 | 0.3
2008-01-02 | 0.109 | 0.098 | 15 | 0.164 | 0.098 | 25 |  |  |  | 0.109 | 0.098 | 15 | 0.164 | 0.098 | 25 |  |  |  | 0.1 | 0.3
2008-01-03 | [18 empty] | 0.1 | 0.3
2008-01-04 | [6 empty] | 0.079 | 0.074 | 17 | [6 empty] | 0.079 | 0.074 | 17 | 0.1 | 0.3
2008-01-05 | [18 empty] | 0.1 | 0.3
2008-01-06 | [18 empty] | 0.1 | 0.3
2008-01-07 | [6 empty] | 0.094 | 0.087 | 35 | [6 empty] | 0.094 | 0.087 | 35 | 0.1 | 0.3
2008-01-08 |  |  |  | 0.101 | 0.084 | 15 | [6 empty] | 0.101 | 0.084 | 15 |  |  |  | 0.1 | 0.3
2008-01-09 | 0.091 | 0.086 | 15 | [6 empty] | 0.091 | 0.086 | 15 | [6 empty] | 0.1 | 0.3
2008-01-10 | [6 empty] | 0.129 | 0.093 | 10 | [6 empty] | 0.129 | 0.093 | 10 | 0.1 | 0.3
2008-01-11 | 0.125 | 0.119 | 20 | 0.136 | 0.112 | 22 |  |  |  | 0.125 | 0.119 | 20 | 0.136 | 0.112 | 22 |  |  |  | 0.1 | 0.3
2008-01-12 | [18 empty] | 0.1 | 0.3
2008-01-13 | [18 empty] | 0.1 | 0.3
2008-01-14 | [6 empty] | 0.065 | 0.057 | 15 | [6 empty] | 0.065 | 0.057 | 15 | 0.1 | 0.3
2008-01-15 | 0.099 | 0.091 | 15 | 0.11 | 0.087 | 20 | 0.061 | 0.175 | 15 | 0.099 | 0.091 | 15 | 0.11 | 0.087 | 20 | 0.061 | 0.175 | 15 | 0.1 | 0.3
2008-01-16 | [6 empty] | 0.14 | 0.07 | 15 | [6 empty] | 0.14 | 0.07 | 15 | 0.1 | 0.3
2008-01-17 | 0.119 | 0.098 | 22 |  |  |  | 0.12 | 0.098 | 17 | 0.119 | 0.098 | 22 |  |  |  | 0.12 | 0.098 | 17 | 0.1 | 0.3
2008-01-18 | [6 empty] | 0.119 | 0.063 | 16 | [6 empty] | 0.119 | 0.063 | 16 | 0.1 | 0.3
2008-01-19 | 0.107 | 0.099 | 22 | 0.125 | 0.103 | 20 |  |  |  | 0.107 | 0.099 | 22 | 0.125 | 0.103 | 20 |  |  |  | 0.1 | 0.3
2008-01-20 | [18 empty] | 0.1 | 0.3
2008-01-21 | [6 empty] | 0.071 | 0.07 | 18 | [6 empty] | 0.071 | 0.07 | 18 | 0.1 | 0.3
2008-01-22 | 0.131 | 0.099 | 30 | 0.134 | 0.099 | 30 |  |  |  | 0.131 | 0.099 | 30 | 0.134 | 0.099 | 30 |  |  |  | 0.1 | 0.3
2008-01-23 | [18 empty] | 0.1 | 0.3
2008-01-24 | 0.179 | 0.168 | 25 | 0.216 | 0.183 | 30 | 0.127 | 0.094 | 12 | 0.179 | 0.168 | 25 | 0.216 | 0.183 | 30 | 0.127 | 0.094 | 12 | 0.1 | 0.3
2008-01-25 | [18 empty] | 0.1 | 0.3
2008-01-26 | [18 empty] | 0.1 | 0.3
2008-01-27 | 0.078 | 0.071 | 14 | 0.088 | 0.084 | 15 | 0.082 | 0.079 | 13 | 0.078 | 0.071 | 14 | 0.088 | 0.084 | 15 | 0.082 | 0.079 | 13 | 0.1 | 0.3
2008-01-28 | [6 empty] | 0.143 | 0.065 | 12 | [6 empty] | 0.143 | 0.065 | 12 | 0.1 | 0.3
2008-01-29 | [18 empty] | 0.1 | 0.3
2008-01-30 | 0.075 | 0.066 | 17 | 0.106 | 0.092 | 17 |  |  |  | 0.075 | 0.066 | 17 | 0.106 | 0.092 | 17 |  |  |  | 0.1 | 0.3
2008-01-31 | [6 empty] | 0.07 | 0.055 | 15 | [6 empty] | 0.07 | 0.055 | 15 | 0.1 | 0.3
2008-02-01 |  |  |  | 0.094 | 0.088 | 15 | [6 empty] | 0.094 | 0.088 | 15 |  |  |  | 0.1 | 0.3
2008-02-02 | 0.071 | 0.07 | 14 | [6 empty] | 0.071 | 0.07 | 14 | [6 empty] | 0.1 | 0.3
2008-02-03 | [6 empty] | 0.085 | 0.064 | 11 | [6 empty] | 0.085 | 0.064 | 11 | 0.1 | 0.3
2008-02-04 |  |  |  | 0.572 | 0.055 | 8 | [6 empty] | 0.572 | 0.055 | 8 |  |  |  | 0.1 | 0.3
2008-02-05 | [6 empty] | 0.066 | 0.063 | 11 | [6 empty] | 0.066 | 0.063 | 11 | 0.1 | 0.3
2008-02-06 | [18 empty] | 0.1 | 0.3
2008-02-07 | 0.115 | 0.111 | 50 | 0.801 | 0.266 | 320 | 0.424 | 0.24 | 140 | 0.115 | 0.111 | 50 | 0.801 | 0.266 | 320 | 0.424 | 0.24 | 140 | 0.1 | 0.3
2008-02-08 | 0.742 | 0.105 | 30 | [6 empty] | 0.742 | 0.105 | 30 | [6 empty] | 0.1 | 0.3
2008-02-09 |  |  |  | 0.144 | 0.088 | 25 | 0.064 | 0.061 | 12 |  |  |  | 0.144 | 0.088 | 25 | 0.064 | 0.061 | 12 | 0.1 | 0.3
2008-02-10 | [18 empty] | 0.1 | 0.3
2008-02-11 | [18 empty] | 0.1 | 0.3
2008-02-12 | [18 empty] | 0.1 | 0.3
2008-02-13 | 0.1 | 0.091 | 22 | [6 empty] | 0.1 | 0.091 | 22 | [6 empty] | 0.1 | 0.3
2008-02-14 |  |  |  | 0.119 | 0.09 | 25 | 0.08 | 0.059 | 16 |  |  |  | 0.119 | 0.09 | 25 | 0.08 | 0.059 | 16 | 0.1 | 0.3
2008-02-15 | 0.125 | 0.1 | 30 |  |  |  | 0.074 | 0.07 | 13 | 0.125 | 0.1 | 30 |  |  |  | 0.074 | 0.07 | 13 | 0.1 | 0.3
2008-02-16 |  |  |  | 0.125 | 0.097 | 30 | 0.078 | 0.063 | 10 |  |  |  | 0.125 | 0.097 | 30 | 0.078 | 0.063 | 10 | 0.1 | 0.3
2008-02-17 | 0.127 | 0.096 | 35 | [6 empty] | 0.127 | 0.096 | 35 | [6 empty] | 0.1 | 0.3
2008-02-18 |  |  |  | 0.115 | 0.098 | 10 | 0.069 | 0.066 | 10 |  |  |  | 0.115 | 0.098 | 10 | 0.069 | 0.066 | 10 | 0.1 | 0.3
2008-02-19 |  | 0.149 | 150 | [7 empty] | 0.149 | 150 | [6 empty] | 0.1 | 0.3
2008-02-20 |  |  |  | 0.442 | 0.162 | 155 | 0.121 | 0.081 | 15 |  |  |  | 0.442 | 0.162 | 155 | 0.121 | 0.081 | 15 | 0.1 | 0.3
2008-02-21 | 0.12 | 0.108 | 25 | [6 empty] | 0.12 | 0.108 | 25 | [6 empty] | 0.1 | 0.3
2008-02-22 |  |  |  | 0.115 | 0.104 | 20 | 0.074 | 0.073 | 13 |  |  |  | 0.115 | 0.104 | 20 | 0.074 | 0.073 | 13 | 0.1 | 0.3
2008-02-23 | 0.153 | 0.124 | 30 | [6 empty] | 0.153 | 0.124 | 30 | [6 empty] | 0.1 | 0.3
2008-02-24 |  |  |  | 0.155 | 0.099 | 30 | [6 empty] | 0.155 | 0.099 | 30 |  |  |  | 0.1 | 0.3
2008-02-25 | 0.134 | 0.109 | 30 |  |  |  | 0.075 | 0.073 | 13 | 0.134 | 0.109 | 30 |  |  |  | 0.075 | 0.073 | 13 | 0.1 | 0.3
2008-02-26 |  |  |  | 0.14 | 0.099 | 30 | [6 empty] | 0.14 | 0.099 | 30 |  |  |  | 0.1 | 0.3
2008-02-27 | 0.127 | 0.12 | 25 |  |  |  | 0.075 | 0.073 | 13 | 0.127 | 0.12 | 25 |  |  |  | 0.075 | 0.073 | 13 | 0.1 | 0.3
2008-02-28 | [18 empty] | 0.1 | 0.3
2008-02-29 | [18 empty] | 0.1 | 0.3
2008-03-01 | [18 empty] | 0.1 | 0.3
2008-03-02 | [18 empty] | 0.1 | 0.3
2008-03-03 | [18 empty] | 0.1 | 0.3
2008-03-04 | [18 empty] | 0.1 | 0.3
2008-03-05 | [18 empty] | 0.1 | 0.3
2008-03-06 | [18 empty] | 0.1 | 0.3
2008-03-07 | [18 empty] | 0.1 | 0.3
2008-03-08 | [18 empty] | 0.1 | 0.3
2008-03-09 | [18 empty] | 0.1 | 0.3
2008-03-10 | [18 empty] | 0.1 | 0.3
2008-03-11 | [18 empty] | 0.1 | 0.3
2008-03-12 | [18 empty] | 0.1 | 0.3
2008-03-13 | [18 empty] | 0.1 | 0.3
2008-03-14 | [18 empty] | 0.1 | 0.3
2008-03-15 | [18 empty] | 0.1 | 0.3
2008-03-16 | [18 empty] | 0.1 | 0.3
2008-03-17 | [18 empty] | 0.1 | 0.3
2008-03-18 | [18 empty] | 0.1 | 0.3
2008-03-19 | [18 empty] | 0.1 | 0.3
2008-03-20 | [18 empty] | 0.1 | 0.3
2008-03-21 | [18 empty] | 0.1 | 0.3
2008-03-22 | [18 empty] | 0.1 | 0.3
2008-03-23 | [18 empty] | 0.1 | 0.3
2008-03-24 | [18 empty] | 0.1 | 0.3
2008-03-25 | [18 empty] | 0.1 | 0.3
2008-03-26 | [18 empty] | 0.1 | 0.3
2008-03-27 | [18 empty] | 0.1 | 0.3
2008-03-28 | [18 empty] | 0.1 | 0.3
2008-03-29 | [18 empty] | 0.1 | 0.3
2008-03-30 | [18 empty] | 0.1 | 0.3
2008-03-31 | [18 empty] | 0.1 | 0.3
2008-04-01 | [18 empty] | 0.1 | 0.3
2008-04-02 | [18 empty] | 0.1 | 0.3
2008-04-03 | 0.081 | 0.075 | 16 |  |  |  | 0.082 | 0.06 | 13 | 0.081 | 0.075 | 16 |  |  |  | 0.082 | 0.06 | 13 | 0.1 | 0.3
2008-04-04 |  |  |  | 0.113 | 0.066 | 17 | [6 empty] | 0.113 | 0.066 | 17 |  |  |  | 0.1 | 0.3
2008-04-05 | [6 empty] | 0.158 | 0.074 | 12 | [6 empty] | 0.158 | 0.074 | 12 | 0.1 | 0.3
2008-04-06 | 0.095 | 0.087 | 12 | 0.074 | 0.071 | 11 |  |  |  | 0.095 | 0.087 | 12 | 0.074 | 0.071 | 11 |  |  |  | 0.1 | 0.3
2008-04-07 | [18 empty] | 0.1 | 0.3
2008-04-08 | [18 empty] | 0.1 | 0.3
2008-04-09 | [6 empty] | 0.141 | 0.08 | 15 | [6 empty] | 0.141 | 0.08 | 15 | 0.1 | 0.3
2008-04-10 | 0.144 | 0.099 | 16 | 0.079 | 0.071 | 12 |  |  |  | 0.144 | 0.099 | 16 | 0.079 | 0.071 | 12 |  |  |  | 0.1 | 0.3
2008-04-11 | [18 empty] | 0.1 | 0.3
2008-04-12 | [18 empty] | 0.1 | 0.3
2008-04-13 | [18 empty] | 0.1 | 0.3
2008-04-14 | [18 empty] | 0.1 | 0.3
2008-04-15 | [18 empty] | 0.1 | 0.3
2008-04-16 | [18 empty] | 0.1 | 0.3
2008-04-17 | [18 empty] | 0.1 | 0.3
2008-04-18 | [18 empty] | 0.1 | 0.3
2008-04-19 | [18 empty] | 0.1 | 0.3
2008-04-20 | [18 empty] | 0.1 | 0.3
2008-04-21 | [18 empty] | 0.1 | 0.3
2008-04-22 | [18 empty] | 0.1 | 0.3
2008-04-23 | [18 empty] | 0.1 | 0.3
2008-04-24 | [18 empty] | 0.1 | 0.3
2008-04-25 | [18 empty] | 0.1 | 0.3
2008-04-26 | 0.165 | 0.092 | 11 | [6 empty] | 0.165 | 0.092 | 11 | [6 empty] | 0.1 | 0.3
2008-04-27 | [6 empty] | 0.108 | 0.072 | 12 | [6 empty] | 0.108 | 0.072 | 12 | 0.1 | 0.3
2008-04-28 |  |  |  | 0.067 | 0.063 | 14 | [6 empty] | 0.067 | 0.063 | 14 |  |  |  | 0.1 | 0.3
2008-04-29 | [18 empty] | 0.1 | 0.3
2008-04-30 | 0.122 | 0.074 | 13 | [6 empty] | 0.122 | 0.074 | 13 | [6 empty] | 0.1 | 0.3
2008-05-01 |  |  |  | 0.059 | 0.054 | 14 | [6 empty] | 0.059 | 0.054 | 14 |  |  |  | 0.1 | 0.3
2008-05-02 | [18 empty] | 0.1 | 0.3
2008-05-03 | 0.079 | 0.072 | 13 | [6 empty] | 0.079 | 0.072 | 13 | [6 empty] | 0.1 | 0.3
2008-05-04 |  |  |  | 0.059 | 0.049 | 12 | [6 empty] | 0.059 | 0.049 | 12 |  |  |  | 0.1 | 0.3
2008-05-05 | [6 empty] | 0.096 | 0.084 | 10 | [6 empty] | 0.096 | 0.084 | 10 | 0.1 | 0.3
2008-05-06 | [18 empty] | 0.1 | 0.3
2008-05-07 | 0.076 | 0.069 | 13 | 0.056 | 0.031 | 9 |  |  |  | 0.076 | 0.069 | 13 | 0.056 | 0.031 | 9 |  |  |  | 0.1 | 0.3
2008-05-08 | [18 empty] | 0.1 | 0.3
2008-05-09 | [18 empty] | 0.1 | 0.3
2008-05-10 | 0.083 | 0.076 | 11 | [6 empty] | 0.083 | 0.076 | 11 | [6 empty] | 0.1 | 0.3
2008-05-11 |  |  |  | 0.062 | 0.058 | 13 | [6 empty] | 0.062 | 0.058 | 13 |  |  |  | 0.1 | 0.3
2008-05-12 | [6 empty] | 0.146 | 0.066 | 14 | [6 empty] | 0.146 | 0.066 | 14 | 0.1 | 0.3
2008-05-13 | [18 empty] | 0.1 | 0.3
2008-05-14 | 0.149 | 0.088 | 12 | [6 empty] | 0.149 | 0.088 | 12 | [6 empty] | 0.1 | 0.3
2008-05-15 |  |  |  | 0.12 | 0.074 | 12 | 0.236 | 0.07 | 13 |  |  |  | 0.12 | 0.074 | 12 | 0.236 | 0.07 | 13 | 0.1 | 0.3
2008-05-16 | [18 empty] | 0.1 | 0.3
2008-05-17 | 0.184 | 0.08 | 17 | [6 empty] | 0.184 | 0.08 | 17 | [6 empty] | 0.1 | 0.3
2008-05-18 |  |  |  | 0.116 | 0.066 | 15 | 0.228 | 0.063 | 20 |  |  |  | 0.116 | 0.066 | 15 | 0.228 | 0.063 | 20 | 0.1 | 0.3
2008-05-19 | 0.325 | 0.086 | 12 | 0.067 | 0.059 | 12 | 0.129 | 0.063 | 20 | 0.325 | 0.086 | 12 | 0.067 | 0.059 | 12 | 0.129 | 0.063 | 20 | 0.1 | 0.3
2008-05-20 | [18 empty] | 0.1 | 0.3
2008-05-21 | 0.148 | 0.098 | 11 | [6 empty] | 0.148 | 0.098 | 11 | [6 empty] | 0.1 | 0.3
2008-05-22 |  |  |  | 0.099 | 0.058 | 20 | [6 empty] | 0.099 | 0.058 | 20 |  |  |  | 0.1 | 0.3
2008-05-23 | [6 empty] | 0.164 | 0.094 | 21 | [6 empty] | 0.164 | 0.094 | 21 | 0.1 | 0.3
2008-05-24 | 0.112 | 0.087 | 11 | [6 empty] | 0.112 | 0.087 | 11 | [6 empty] | 0.1 | 0.3
2008-05-25 |  |  |  | 0.09 | 0.081 | 11 | [6 empty] | 0.09 | 0.081 | 11 |  |  |  | 0.1 | 0.3
2008-05-26 | [18 empty] | 0.1 | 0.3
2008-05-27 | 0.118 | 0.095 | 12 | [6 empty] | 0.118 | 0.095 | 12 | [6 empty] | 0.1 | 0.3
2008-05-28 |  |  |  | 0.097 | 0.075 | 12 | [6 empty] | 0.097 | 0.075 | 12 |  |  |  | 0.1 | 0.3
2008-05-29 | 0.105 | 0.083 | 11 | [6 empty] | 0.105 | 0.083 | 11 | [6 empty] | 0.1 | 0.3
2008-05-30 | [18 empty] | 0.1 | 0.3
2008-05-31 |  |  |  | 0.124 | 0.076 | 13 | 0.156 | 0.089 | 30 |  |  |  | 0.124 | 0.076 | 13 | 0.156 | 0.089 | 30 | 0.1 | 0.3
2008-06-01 | 0.125 | 0.096 | 13 | [6 empty] | 0.125 | 0.096 | 13 | [6 empty] | 0.1 | 0.3
2008-06-02 | [18 empty] | 0.1 | 0.3
2008-06-03 | 0.154 | 0.098 | 19 | 0.125 | 0.089 | 17 |  |  |  | 0.154 | 0.098 | 19 | 0.125 | 0.089 | 17 |  |  |  | 0.1 | 0.3
2008-06-04 | 0.202 | 0.092 | 20 | 0.261 | 0.091 | 20 |  |  |  | 0.202 | 0.092 | 20 | 0.261 | 0.091 | 20 |  |  |  | 0.1 | 0.3
2008-06-05 | [6 empty] | 0.108 | 0.145 | 20 | [6 empty] | 0.108 | 0.145 | 20 | 0.1 | 0.3
2008-06-06 | 0.137 | 0.099 | 17 | 0.139 | 0.109 | 30 |  |  |  | 0.137 | 0.099 | 17 | 0.139 | 0.109 | 30 |  |  |  | 0.1 | 0.3
2008-06-07 | 0.151 | 0.095 | 16 | 0.124 | 0.099 | 21 | 0.201 | 0.095 | 25 | 0.151 | 0.095 | 16 | 0.124 | 0.099 | 21 | 0.201 | 0.095 | 25 | 0.1 | 0.3
2008-06-08 | [18 empty] | 0.1 | 0.3
2008-06-09 | [18 empty] | 0.1 | 0.3
2008-06-10 | [18 empty] | 0.1 | 0.3
2008-06-11 | [18 empty] | 0.1 | 0.3
2008-06-12 | [18 empty] | 0.1 | 0.3
2008-06-13 | [18 empty] | 0.1 | 0.3
2008-06-14 | [18 empty] | 0.1 | 0.3
2008-06-15 | [18 empty] | 0.1 | 0.3
2008-06-16 | [18 empty] | 0.1 | 0.3
2008-06-17 | [18 empty] | 0.1 | 0.3
2008-06-18 | [18 empty] | 0.1 | 0.3
2008-06-19 | [18 empty] | 0.1 | 0.3
2008-06-20 | [18 empty] | 0.1 | 0.3
2008-06-21 | [18 empty] | 0.1 | 0.3
2008-06-22 | [18 empty] | 0.1 | 0.3
2008-06-23 | [18 empty] | 0.1 | 0.3
2008-06-24 | [18 empty] | 0.1 | 0.3
2008-06-25 | [18 empty] | 0.1 | 0.3
2008-06-26 | [18 empty] | 0.1 | 0.3
2008-06-27 | [18 empty] | 0.1 | 0.3
2008-06-28 | [18 empty] | 0.1 | 0.3
2008-06-29 | 0.113 | 0.087 | 13 | 0.118 | 0.096 | 17 |  |  |  | 0.113 | 0.087 | 13 | 0.118 | 0.096 | 17 |  |  |  | 0.1 | 0.3
2008-06-30 | 0.111 | 0.092 | 12 | 0.095 | 0.088 | 10 | 0.185 | 0.093 | 25 | 0.111 | 0.092 | 12 | 0.095 | 0.088 | 10 | 0.185 | 0.093 | 25 | 0.1 | 0.3
2008-07-01 | [18 empty] | 0.1 | 0.3
2008-07-02 | 0.131 | 0.117 | 30 | [6 empty] | 0.131 | 0.117 | 30 | [6 empty] | 0.1 | 0.3
2008-07-03 |  |  |  | 0.072 | 0.066 | 22 | 0.154 | 0.085 | 23 |  |  |  | 0.072 | 0.066 | 22 | 0.154 | 0.085 | 23 | 0.1 | 0.3
2008-07-04 | [18 empty] | 0.1 | 0.3
2008-07-05 | 0.126 | 0.092 | 15 | [6 empty] | 0.126 | 0.092 | 15 | [6 empty] | 0.1 | 0.3
2008-07-06 |  |  |  | 0.104 | 0.085 | 10 | 0.208 | 0.095 | 25 |  |  |  | 0.104 | 0.085 | 10 | 0.208 | 0.095 | 25 | 0.1 | 0.3
2008-07-07 | 0.142 | 0.07 | 20 | [6 empty] | 0.142 | 0.07 | 20 | [6 empty] | 0.1 | 0.3
2008-07-08 | 0.12 | 0.073 | 16 | [6 empty] | 0.12 | 0.073 | 16 | [6 empty] | 0.1 | 0.3
2008-07-09 | [6 empty] | 0.17 | 0.094 | 22 | [6 empty] | 0.17 | 0.094 | 22 | 0.1 | 0.3
2008-07-10 | 0.106 | 0.073 | 16 | 0.131 | 0.103 | 25 |  |  |  | 0.106 | 0.073 | 16 | 0.131 | 0.103 | 25 |  |  |  | 0.1 | 0.3
2008-07-11 | 0.135 | 0.084 | 14 |  |  |  | 0.237 | 0.09 | 21 | 0.135 | 0.084 | 14 |  |  |  | 0.237 | 0.09 | 21 | 0.1 | 0.3
2008-07-12 | [18 empty] | 0.1 | 0.3
2008-07-13 | 0.127 | 0.087 | 11 | 0.112 | 0.055 | 15 | 0.167 | 0.092 | 18 | 0.127 | 0.087 | 11 | 0.112 | 0.055 | 15 | 0.167 | 0.092 | 18 | 0.1 | 0.3
2008-07-14 | 0.126 | 0.086 | 12 | [6 empty] | 0.126 | 0.086 | 12 | [6 empty] | 0.1 | 0.3
2008-07-15 | 0.135 | 0.095 | 13 | 0.148 | 0.088 | 11 | 0.16 | 0.088 | 18 | 0.135 | 0.095 | 13 | 0.148 | 0.088 | 11 | 0.16 | 0.088 | 18 | 0.1 | 0.3
2008-07-16 | 0.637 | 0.115 | 52 | 0.701 | 0.17 | 92 |  |  |  | 0.637 | 0.115 | 52 | 0.701 | 0.17 | 92 |  |  |  | 0.1 | 0.3
2008-07-17 | [6 empty] | 0.166 | 0.094 | 22 | [6 empty] | 0.166 | 0.094 | 22 | 0.1 | 0.3
2008-07-18 | 0.18 | 0.093 | 19 | [6 empty] | 0.18 | 0.093 | 19 | [6 empty] | 0.1 | 0.3
2008-07-19 |  |  |  | 0.211 | 0.088 | 16 | [6 empty] | 0.211 | 0.088 | 16 |  |  |  | 0.1 | 0.3
2008-07-20 | 0.21 | 0.098 | 25 |  |  |  | 0.198 | 0.077 | 22 | 0.21 | 0.098 | 25 |  |  |  | 0.198 | 0.077 | 22 | 0.1 | 0.3
2008-07-21 | 0.187 | 0.094 | 17 | 0.15 | 0.063 | 17 |  |  |  | 0.187 | 0.094 | 17 | 0.15 | 0.063 | 17 |  |  |  | 0.1 | 0.3
2008-07-22 | [18 empty] | 0.1 | 0.3
2008-07-23 | 0.199 | 0.092 | 19 |  |  |  | 0.236 | 0.086 | 30 | 0.199 | 0.092 | 19 |  |  |  | 0.236 | 0.086 | 30 | 0.1 | 0.3
2008-07-24 | 0.201 | 0.099 | 27 | 0.152 | 0.068 | 15 |  |  |  | 0.201 | 0.099 | 27 | 0.152 | 0.068 | 15 |  |  |  | 0.1 | 0.3
2008-07-25 | 0.236 | 0.098 | 26 | 0.169 | 0.078 | 15 | 0.213 | 0.09 | 20 | 0.236 | 0.098 | 26 | 0.169 | 0.078 | 15 | 0.213 | 0.09 | 20 | 0.1 | 0.3
2008-07-26 | [18 empty] | 0.1 | 0.3
2008-07-27 | 0.227 | 0.108 | 35 | 0.156 | 0.09 | 15 |  |  |  | 0.227 | 0.108 | 35 | 0.156 | 0.09 | 15 |  |  |  | 0.1 | 0.3
2008-07-28 | 0.185 | 0.106 | 36 |  |  |  | 0.185 | 0.088 | 21 | 0.185 | 0.106 | 36 |  |  |  | 0.185 | 0.088 | 21 | 0.1 | 0.3
2008-07-29 | 0.202 | 0.117 | 45 | 0.184 | 0.098 | 26 |  |  |  | 0.202 | 0.117 | 45 | 0.184 | 0.098 | 26 |  |  |  | 0.1 | 0.3
2008-07-30 | [18 empty] | 0.1 | 0.3
2008-07-31 | 0.227 | 0.108 | 35 | 0.156 | 0.09 | 15 |  |  |  | 0.227 | 0.108 | 35 | 0.156 | 0.09 | 15 |  |  |  | 0.1 | 0.3
2008-08-01 |  |  |  | 0.205 | 0.085 | 20 | [6 empty] | 0.205 | 0.085 | 20 |  |  |  | 0.1 | 0.3
2008-08-02 | [18 empty] | 0.1 | 0.3
2008-08-03 | 0.242 | 0.09 | 27 | 0.23 | 0.092 | 19 | 0.356 | 0.09 | 33 | 0.242 | 0.09 | 27 | 0.23 | 0.092 | 19 | 0.356 | 0.09 | 33 | 0.1 | 0.3
2008-08-04 | [18 empty] | 0.1 | 0.3
2008-08-05 | [6 empty] | 0.251 | 0.09 | 25 | [6 empty] | 0.251 | 0.09 | 25 | 0.1 | 0.3
2008-08-06 | 0.234 | 0.103 | 45 | [6 empty] | 0.234 | 0.103 | 45 | [6 empty] | 0.1 | 0.3
2008-08-07 |  |  |  | 0.189 | 0.088 | 20 | 0.229 | 0.083 | 19 |  |  |  | 0.189 | 0.088 | 20 | 0.229 | 0.083 | 19 | 0.1 | 0.3
2008-08-08 | 0.243 | 0.104 | 30 |  |  |  | 0.189 | 0.089 | 20 | 0.243 | 0.104 | 30 |  |  |  | 0.189 | 0.089 | 20 | 0.1 | 0.3
2008-08-09 | [18 empty] | 0.1 | 0.3
2008-08-10 | 0.213 | 0.098 | 23 | 0.209 | 0.094 | 16 | 0.187 | 0.086 | 25 | 0.213 | 0.098 | 23 | 0.209 | 0.094 | 16 | 0.187 | 0.086 | 25 | 0.1 | 0.3
2008-08-11 | [18 empty] | 0.1 | 0.3
2008-08-12 | [18 empty] | 0.1 | 0.3
2008-08-13 | 0.159 | 0.096 | 17 | 0.15 | 0.088 | 14 | 0.18 | 0.091 | 27 | 0.159 | 0.096 | 17 | 0.15 | 0.088 | 14 | 0.18 | 0.091 | 27 | 0.1 | 0.3
2008-08-14 | [18 empty] | 0.1 | 0.3
2008-08-15 | 0.202 | 0.091 | 20 |  |  |  | 0.238 | 0.09 | 25 | 0.202 | 0.091 | 20 |  |  |  | 0.238 | 0.09 | 25 | 0.1 | 0.3
2008-08-16 |  |  |  | 0.16 | 0.086 | 17 | [6 empty] | 0.16 | 0.086 | 17 |  |  |  | 0.1 | 0.3
2008-08-17 | [6 empty] | 0.198 | 0.091 | 25 | [6 empty] | 0.198 | 0.091 | 25 | 0.1 | 0.3
2008-08-18 | 0.201 | 0.097 | 30 | [6 empty] | 0.201 | 0.097 | 30 | [6 empty] | 0.1 | 0.3
2008-08-19 | [6 empty] | 0.223 | 0.085 | 30 | [6 empty] | 0.223 | 0.085 | 30 | 0.1 | 0.3
2008-08-20 | 0.182 | 0.097 | 25 | 0.145 | 0.086 | 15 |  |  |  | 0.182 | 0.097 | 25 | 0.145 | 0.086 | 15 |  |  |  | 0.1 | 0.3
2008-08-21 | [18 empty] | 0.1 | 0.3
2008-08-22 | [18 empty] | 0.1 | 0.3
2008-08-23 | 0.212 | 0.098 | 23 | 0.183 | 0.092 | 20 |  |  |  | 0.212 | 0.098 | 23 | 0.183 | 0.092 | 20 |  |  |  | 0.1 | 0.3
2008-08-24 | 0.184 | 0.088 | 20 | [6 empty] | 0.184 | 0.088 | 20 | [6 empty] | 0.1 | 0.3
2008-08-25 |  |  |  | 0.163 | 0.078 | 14 | 0.175 | 0.068 | 26 |  |  |  | 0.163 | 0.078 | 14 | 0.175 | 0.068 | 26 | 0.1 | 0.3
2008-08-26 | 0.181 | 0.07 | 30 | [6 empty] | 0.181 | 0.07 | 30 | [6 empty] | 0.1 | 0.3
2008-08-27 | [6 empty] | 0.17 | 0.096 | 20 | [6 empty] | 0.17 | 0.096 | 20 | 0.1 | 0.3
2008-08-28 |  |  |  | 0.145 | 0.058 | 20 | [6 empty] | 0.145 | 0.058 | 20 |  |  |  | 0.1 | 0.3
2008-08-29 | 0.184 | 0.097 | 21 | [6 empty] | 0.184 | 0.097 | 21 | [6 empty] | 0.1 | 0.3
2008-08-30 |  |  |  | 0.189 | 0.085 | 18 | [6 empty] | 0.189 | 0.085 | 18 |  |  |  | 0.1 | 0.3
2008-08-31 | [6 empty] | 0.238 | 0.09 | 35 | [6 empty] | 0.238 | 0.09 | 35 | 0.1 | 0.3
2008-09-01 | [18 empty] | 0.1 | 0.3
2008-09-02 | [18 empty] | 0.1 | 0.3
2008-09-03 | [6 empty] | 0.37 | 0.112 | 45 | [6 empty] | 0.37 | 0.112 | 45 | 0.1 | 0.3
2008-09-04 | [18 empty] | 0.1 | 0.3
2008-09-05 |  |  |  | 0.22 | 0.099 | 37 | [6 empty] | 0.22 | 0.099 | 37 |  |  |  | 0.1 | 0.3
2008-09-06 | 0.23 | 0.097 | 27 | [6 empty] | 0.23 | 0.097 | 27 | [6 empty] | 0.1 | 0.3
2008-09-07 | 0.236 | 0.099 | 61 |  |  |  | 0.254 | 0.088 | 35 | 0.236 | 0.099 | 61 |  |  |  | 0.254 | 0.088 | 35 | 0.1 | 0.3
2008-09-08 | 0.441 | 0.137 | 159 | 0.193 | 0.137 | 40 |  |  |  | 0.441 | 0.137 | 159 | 0.193 | 0.137 | 40 |  |  |  | 0.1 | 0.3
2008-09-09 | [6 empty] | 0.324 | 0.119 | 45 | [6 empty] | 0.324 | 0.119 | 45 | 0.1 | 0.3
2008-09-10 | [18 empty] | 0.1 | 0.3
2008-09-11 | [18 empty] | 0.1 | 0.3
2008-09-12 | 0.184 | 0.097 | 37 | 0.126 | 0.081 | 24 |  |  |  | 0.184 | 0.097 | 37 | 0.126 | 0.081 | 24 |  |  |  | 0.1 | 0.3
2008-09-13 | [6 empty] | 0.211 | 0.124 | 30 | [6 empty] | 0.211 | 0.124 | 30 | 0.1 | 0.3
2008-09-14 | [18 empty] | 0.1 | 0.3
2008-09-15 | [18 empty] | 0.1 | 0.3
2008-09-16 | [6 empty] | 0.323 | 0.13 | 40 | [6 empty] | 0.323 | 0.13 | 40 | 0.1 | 0.3
2008-09-17 | 0.236 | 0.099 | 35 | 0.146 | 0.098 | 23 |  |  |  | 0.236 | 0.099 | 35 | 0.146 | 0.098 | 23 |  |  |  | 0.1 | 0.3
2008-09-18 | [18 empty] | 0.1 | 0.3
2008-09-19 | [18 empty] | 0.1 | 0.3
2008-09-20 | [6 empty] | 0.268 | 0.097 | 35 | [6 empty] | 0.268 | 0.097 | 35 | 0.1 | 0.3
2008-09-21 | 0.271 | 0.139 | 30 | 0.157 | 0.112 | 38 | 0.038 | 0.038 | 20 | 0.271 | 0.139 | 30 | 0.157 | 0.112 | 38 | 0.038 | 0.038 | 20 | 0.1 | 0.3
2008-09-22 | [18 empty] | 0.1 | 0.3
2008-09-23 | [18 empty] | 0.1 | 0.3
2008-09-24 | 0.355 | 0.152 | 35 | 0.167 | 0.147 | 30 | 0.264 | 0.098 | 43 | 0.355 | 0.152 | 35 | 0.167 | 0.147 | 30 | 0.264 | 0.098 | 43 | 0.1 | 0.3
2008-09-25 | [18 empty] | 0.1 | 0.3
2008-09-26 | [18 empty] | 0.1 | 0.3
2008-09-27 | 0.264 | 0.172 | 30 |  |  |  | 0.207 | 0.117 | 30 | 0.264 | 0.172 | 30 |  |  |  | 0.207 | 0.117 | 30 | 0.1 | 0.3
2008-09-28 |  |  |  | 0.169 | 0.115 | 30 | [6 empty] | 0.169 | 0.115 | 30 |  |  |  | 0.1 | 0.3
2008-09-29 | [18 empty] | 0.1 | 0.3
2008-09-30 | [18 empty] | 0.1 | 0.3
2008-10-01 | [6 empty] | 0.193 | 0.11 | 30 | [6 empty] | 0.193 | 0.11 | 30 | 0.1 | 0.3
2008-10-02 | 0.244 | 0.145 | 30 | 0.149 | 0.099 | 30 |  |  |  | 0.244 | 0.145 | 30 | 0.149 | 0.099 | 30 |  |  |  | 0.1 | 0.3
2008-10-03 | [18 empty] | 0.1 | 0.3
2008-10-04 | [6 empty] | 0.183 | 0.092 | 29 | [6 empty] | 0.183 | 0.092 | 29 | 0.1 | 0.3
2008-10-05 | 0.254 | 0.138 | 32 | 0.149 | 0.109 | 28 |  |  |  | 0.254 | 0.138 | 32 | 0.149 | 0.109 | 28 |  |  |  | 0.1 | 0.3
2008-10-06 |  |  |  | 0.115 | 0.119 | 28 | [6 empty] | 0.115 | 0.119 | 28 |  |  |  | 0.1 | 0.3
2008-10-07 | [6 empty] | 0.207 | 0.097 | 30 | [6 empty] | 0.207 | 0.097 | 30 | 0.1 | 0.3
2008-10-08 | [18 empty] | 0.1 | 0.3
2008-10-09 | [18 empty] | 0.1 | 0.3
2008-10-10 | 0.179 | 0.126 | 25 |  |  |  | 0.244 | 0.1 | 30 | 0.179 | 0.126 | 25 |  |  |  | 0.244 | 0.1 | 30 | 0.1 | 0.3
2008-10-11 | [18 empty] | 0.1 | 0.3
2008-10-12 |  |  |  | 0.172 | 0.109 | 30 | 0.195 | 0.102 | 25 |  |  |  | 0.172 | 0.109 | 30 | 0.195 | 0.102 | 25 | 0.1 | 0.3
2008-10-13 | [6 empty] | 0.198 | 0.081 | 30 | [6 empty] | 0.198 | 0.081 | 30 | 0.1 | 0.3
2008-10-14 | [18 empty] | 0.1 | 0.3
2008-10-15 | [6 empty] | 0.187 | 0.095 | 30 | [6 empty] | 0.187 | 0.095 | 30 | 0.1 | 0.3
2008-10-16 | [18 empty] | 0.1 | 0.3
2008-10-17 | [6 empty] | 0.221 | 0.088 | 30 | [6 empty] | 0.221 | 0.088 | 30 | 0.1 | 0.3
2008-10-18 | [6 empty] | 0.177 | 0.085 | 29 | [6 empty] | 0.177 | 0.085 | 29 | 0.1 | 0.3
2008-10-19 | 0.247 | 0.139 | 32 | [6 empty] | 0.247 | 0.139 | 32 | [6 empty] | 0.1 | 0.3
2008-10-20 |  |  |  | 0.273 | 0.223 | 38 | 0.249 | 0.102 | 23 |  |  |  | 0.273 | 0.223 | 38 | 0.249 | 0.102 | 23 | 0.1 | 0.3
2008-10-21 | [18 empty] | 0.1 | 0.3
2008-10-22 | 0.245 | 0.192 | 30 | 0.207 | 0.199 | 30 | 0.17 | 0.097 | 30 | 0.245 | 0.192 | 30 | 0.207 | 0.199 | 30 | 0.17 | 0.097 | 30 | 0.1 | 0.3
2008-10-23 | [18 empty] | 0.1 | 0.3
2008-10-24 | [18 empty] | 0.1 | 0.3
2008-10-25 | 0.161 | 0.144 | 31 | 0.13 | 0.099 | 29 | 0.164 | 0.091 | 24 | 0.161 | 0.144 | 31 | 0.13 | 0.099 | 29 | 0.164 | 0.091 | 24 | 0.1 | 0.3
2008-10-26 | [18 empty] | 0.1 | 0.3
2008-10-27 | [6 empty] | 0.441 | 0.138 | 28 | [6 empty] | 0.441 | 0.138 | 28 | 0.1 | 0.3
2008-10-28 | [18 empty] | 0.1 | 0.3
2008-10-29 |  |  |  | 0.078 | 0.076 | 15 | [6 empty] | 0.078 | 0.076 | 15 |  |  |  | 0.1 | 0.3
2008-10-30 | 0.15 | 0.064 | 12 |  |  |  | 0.151 | 0.093 | 32 | 0.15 | 0.064 | 12 |  |  |  | 0.151 | 0.093 | 32 | 0.1 | 0.3
2008-10-31 | [18 empty] | 0.1 | 0.3
2008-11-01 |  |  |  | 0.127 | 0.086 | 12 | [6 empty] | 0.127 | 0.086 | 12 |  |  |  | 0.1 | 0.3
2008-11-02 | 0.226 | 0.164 | 30 |  |  |  | 0.127 | 0.096 | 25 | 0.226 | 0.164 | 30 |  |  |  | 0.127 | 0.096 | 25 | 0.1 | 0.3
2008-11-03 |  |  |  | 0.241 | 0.13 | 30 | [6 empty] | 0.241 | 0.13 | 30 |  |  |  | 0.1 | 0.3
2008-11-04 | 0.178 | 0.131 | 12 | [6 empty] | 0.178 | 0.131 | 12 | [6 empty] | 0.1 | 0.3
2008-11-05 | [6 empty] | 0.127 | 0.109 | 20 | [6 empty] | 0.127 | 0.109 | 20 | 0.1 | 0.3
2008-11-06 |  |  |  | 0.161 | 0.117 | 21 | [6 empty] | 0.161 | 0.117 | 21 |  |  |  | 0.1 | 0.3
2008-11-07 | 0.155 | 0.09 | 18 | [6 empty] | 0.155 | 0.09 | 18 | [6 empty] | 0.1 | 0.3
2008-11-08 | [6 empty] | 0.116 | 0.098 | 20 | [6 empty] | 0.116 | 0.098 | 20 | 0.1 | 0.3
2008-11-09 |  |  |  | 0.144 | 0.085 | 20 | [6 empty] | 0.144 | 0.085 | 20 |  |  |  | 0.1 | 0.3
2008-11-10 | 0.166 | 0.086 | 22 | [6 empty] | 0.166 | 0.086 | 22 | [6 empty] | 0.1 | 0.3
2008-11-11 | [6 empty] | 0.164 | 0.098 | 30 | [6 empty] | 0.164 | 0.098 | 30 | 0.1 | 0.3
2008-11-12 |  |  |  | 0.111 | 0.085 | 15 | [6 empty] | 0.111 | 0.085 | 15 |  |  |  | 0.1 | 0.3
2008-11-13 | 0.117 | 0.088 | 17 | [6 empty] | 0.117 | 0.088 | 17 | [6 empty] | 0.1 | 0.3
2008-11-14 | [6 empty] | 0.131 | 0.113 | 28 | [6 empty] | 0.131 | 0.113 | 28 | 0.1 | 0.3
2008-11-15 |  |  |  | 0.156 | 0.097 | 26 | [6 empty] | 0.156 | 0.097 | 26 |  |  |  | 0.1 | 0.3
2008-11-16 | 0.136 | 0.098 | 25 | [6 empty] | 0.136 | 0.098 | 25 | [6 empty] | 0.1 | 0.3
2008-11-17 |  |  |  | 0.157 | 0.096 | 21 | 0.202 | 0.127 | 30 |  |  |  | 0.157 | 0.096 | 21 | 0.202 | 0.127 | 30 | 0.1 | 0.3
2008-11-18 | [18 empty] | 0.1 | 0.3
2008-11-19 | 0.129 | 0.099 | 18 | 0.193 | 0.095 | 20 | 3 | 1.461 | 32 | 0.129 | 0.099 | 18 | 0.193 | 0.095 | 20 | 3 | 1.461 | 32 | 0.1 | 0.3
2008-11-20 | [18 empty] | 0.1 | 0.3
2008-11-21 | 0.151 | 0.099 | 26 |  |  |  | 0.222 | 0.186 | 30 | 0.151 | 0.099 | 26 |  |  |  | 0.222 | 0.186 | 30 | 0.1 | 0.3
2008-11-22 |  |  |  | 0.183 | 0.099 | 19 | [6 empty] | 0.183 | 0.099 | 19 |  |  |  | 0.1 | 0.3
2008-11-23 | 0.142 | 0.121 | 38 | [6 empty] | 0.142 | 0.121 | 38 | [6 empty] | 0.1 | 0.3
2008-11-24 | [6 empty] | 0.256 | 0.214 | 34 | [6 empty] | 0.256 | 0.214 | 34 | 0.1 | 0.3
2008-11-25 | 0.369 | 0.361 | 30 | 0.269 | 0.197 | 30 |  |  |  | 0.369 | 0.361 | 30 | 0.269 | 0.197 | 30 |  |  |  | 0.1 | 0.3
2008-11-26 | [18 empty] | 0.1 | 0.3
2008-11-27 | [18 empty] | 0.1 | 0.3
2008-11-28 |  |  |  | 0.122 | 0.094 | 13 | 0.153 | 0.09 | 20 |  |  |  | 0.122 | 0.094 | 13 | 0.153 | 0.09 | 20 | 0.1 | 0.3
2008-11-29 | 0.12 | 0.092 | 17 | [6 empty] | 0.12 | 0.092 | 17 | [6 empty] | 0.1 | 0.3
2008-11-30 | [18 empty] | 0.1 | 0.3
2008-12-01 |  |  |  | 0.118 | 0.091 | 12 | [6 empty] | 0.118 | 0.091 | 12 |  |  |  | 0.1 | 0.3
2008-12-02 | 0.22 | 0.188 | 30 |  |  |  | 0.229 | 0.161 | 30 | 0.22 | 0.188 | 30 |  |  |  | 0.229 | 0.161 | 30 | 0.1 | 0.3
2008-12-03 | [18 empty] | 0.1 | 0.3
2008-12-04 |  |  |  | 0.289 | 0.289 | 32 | [6 empty] | 0.289 | 0.289 | 32 |  |  |  | 0.1 | 0.3
2008-12-05 | [18 empty] | 0.1 | 0.3
2008-12-06 | [6 empty] | 0.15 | 0.15 | 30 | [6 empty] | 0.15 | 0.15 | 30 | 0.1 | 0.3
2008-12-07 | 0.099 | 0.092 | 12 | 0.085 | 0.072 | 12 |  |  |  | 0.099 | 0.092 | 12 | 0.085 | 0.072 | 12 |  |  |  | 0.1 | 0.3
2008-12-08 | [18 empty] | 0.1 | 0.3
2008-12-09 | [6 empty] | 0.13 | 0.103 | 25 | [6 empty] | 0.13 | 0.103 | 25 | 0.1 | 0.3
2008-12-10 | 0.114 | 0.106 | 13 | [6 empty] | 0.114 | 0.106 | 13 | [6 empty] | 0.1 | 0.3
2008-12-11 | [18 empty] | 0.1 | 0.3
2008-12-12 | [6 empty] | 0.145 | 0.12 | 30 | [6 empty] | 0.145 | 0.12 | 30 | 0.1 | 0.3
2008-12-13 | 0.086 | 0.079 | 12 | [6 empty] | 0.086 | 0.079 | 12 | [6 empty] | 0.1 | 0.3
2008-12-14 |  |  |  | 0.079 | 0.063 | 11 | 0.142 | 0.11 | 30 |  |  |  | 0.079 | 0.063 | 11 | 0.142 | 0.11 | 30 | 0.1 | 0.3
2008-12-15 | [18 empty] | 0.1 | 0.3
2008-12-16 |  |  |  | 0.087 | 0.069 | 17 | 0.116 | 0.105 | 25 |  |  |  | 0.087 | 0.069 | 17 | 0.116 | 0.105 | 25 | 0.1 | 0.3
2008-12-17 |  |  |  | 0.088 | 0.075 | 12 | [6 empty] | 0.088 | 0.075 | 12 |  |  |  | 0.1 | 0.3
2008-12-18 | [18 empty] | 0.1 | 0.3
2008-12-19 | [6 empty] | 0.332 | 0.105 | 21 | [6 empty] | 0.332 | 0.105 | 21 | 0.1 | 0.3
2008-12-20 | 0.12 | 0.1 | 21 | 0.107 | 0.096 | 12 |  |  |  | 0.12 | 0.1 | 21 | 0.107 | 0.096 | 12 |  |  |  | 0.1 | 0.3
2008-12-21 | [18 empty] | 0.1 | 0.3
2008-12-22 | [18 empty] | 0.1 | 0.3
2008-12-23 |  |  |  | 0.096 | 0.081 | 12 | [6 empty] | 0.096 | 0.081 | 12 |  |  |  | 0.1 | 0.3
2008-12-24 | [6 empty] | 0.169 | 0.064 | 12 | [6 empty] | 0.169 | 0.064 | 12 | 0.1 | 0.3
2008-12-25 | [18 empty] | 0.1 | 0.3
2008-12-26 | [18 empty] | 0.1 | 0.3
2008-12-27 | [18 empty] | 0.1 | 0.3
2008-12-28 | [18 empty] | 0.1 | 0.3
2008-12-29 | [18 empty] | 0.1 | 0.3
2008-12-30 | [18 empty] | 0.1 | 0.3
2008-12-31 | [18 empty] | 0.1 | 0.3
Note on C15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on D15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on E15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on F15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on G15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on H15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on I15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on J15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on K15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on L15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on M15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on N15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on O15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on P15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on Q15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on R15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on S15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on T15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Clear Database

## Filters7-12BWData (hidden)
Data input screen for filter backwash data.
For filters with filter-to-waste (FTW) capability, input three values per backwash: 1) max. turbidity during FTW period,
2) turbidity at end of FTW period and 3) FTW time.
For filters without FTW capability, input two values per backwash: 1) max. turbidity during initial 15 minutes of filter run
and 2) turbidity after 15 minutes of filter run.
Filter | 7 |  |  | 8 |  |  | 9 |  |  | 10 |  |  | 11 |  |  | 12
Description
Goal @ RTS (NTU) | 0.3 | 0.1 |  | 0.3 | 0.1 |  | 0.3 | 0.1 |  | 0.3 | 0.1 |  | 0.3 | 0.1 |  | 0.3 | 0.1
% values < Goal | 94.2857 | 68.8679 |  | 95.9596 | 77.7778 |  | 92.3077 | 75.9615 |  | 94.2857 | 68.8679 |  | 95.9596 | 77.7778 |  | 92.3077 | 75.9615
95th % NTU | 0.3142 | 0.161 |  | 0.2746 | 0.1844 |  | 0.3308 | 0.15935 |  | 0.3142 | 0.161 |  | 0.2746 | 0.1844 |  | 0.3308 | 0.15935
| Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min) | Max. Turbidity (NTU) | RTS Turbidity (NTU) | FTW Time (min)
2008-01-01 | [6 empty] | 0.101 | 0.059 | 15 | [6 empty] | 0.101 | 0.059 | 15 | 0.1 | 0.3
2008-01-02 | 0.109 | 0.098 | 15 | 0.164 | 0.098 | 25 |  |  |  | 0.109 | 0.098 | 15 | 0.164 | 0.098 | 25 |  |  |  | 0.1 | 0.3
2008-01-03 | [18 empty] | 0.1 | 0.3
2008-01-04 | [6 empty] | 0.079 | 0.074 | 17 | [6 empty] | 0.079 | 0.074 | 17 | 0.1 | 0.3
2008-01-05 | [18 empty] | 0.1 | 0.3
2008-01-06 | [18 empty] | 0.1 | 0.3
2008-01-07 | [6 empty] | 0.094 | 0.087 | 35 | [6 empty] | 0.094 | 0.087 | 35 | 0.1 | 0.3
2008-01-08 |  |  |  | 0.101 | 0.084 | 15 | [6 empty] | 0.101 | 0.084 | 15 |  |  |  | 0.1 | 0.3
2008-01-09 | 0.091 | 0.086 | 15 | [6 empty] | 0.091 | 0.086 | 15 | [6 empty] | 0.1 | 0.3
2008-01-10 | [6 empty] | 0.129 | 0.093 | 10 | [6 empty] | 0.129 | 0.093 | 10 | 0.1 | 0.3
2008-01-11 | 0.125 | 0.119 | 20 | 0.136 | 0.112 | 22 |  |  |  | 0.125 | 0.119 | 20 | 0.136 | 0.112 | 22 |  |  |  | 0.1 | 0.3
2008-01-12 | [18 empty] | 0.1 | 0.3
2008-01-13 | [18 empty] | 0.1 | 0.3
2008-01-14 | [6 empty] | 0.065 | 0.057 | 15 | [6 empty] | 0.065 | 0.057 | 15 | 0.1 | 0.3
2008-01-15 | 0.099 | 0.091 | 15 | 0.11 | 0.087 | 20 | 0.061 | 0.175 | 15 | 0.099 | 0.091 | 15 | 0.11 | 0.087 | 20 | 0.061 | 0.175 | 15 | 0.1 | 0.3
2008-01-16 | [6 empty] | 0.14 | 0.07 | 15 | [6 empty] | 0.14 | 0.07 | 15 | 0.1 | 0.3
2008-01-17 | 0.119 | 0.098 | 22 |  |  |  | 0.12 | 0.098 | 17 | 0.119 | 0.098 | 22 |  |  |  | 0.12 | 0.098 | 17 | 0.1 | 0.3
2008-01-18 | [6 empty] | 0.119 | 0.063 | 16 | [6 empty] | 0.119 | 0.063 | 16 | 0.1 | 0.3
2008-01-19 | 0.107 | 0.099 | 22 | 0.125 | 0.103 | 20 |  |  |  | 0.107 | 0.099 | 22 | 0.125 | 0.103 | 20 |  |  |  | 0.1 | 0.3
2008-01-20 | [18 empty] | 0.1 | 0.3
2008-01-21 | [6 empty] | 0.071 | 0.07 | 18 | [6 empty] | 0.071 | 0.07 | 18 | 0.1 | 0.3
2008-01-22 | 0.131 | 0.099 | 30 | 0.134 | 0.099 | 30 |  |  |  | 0.131 | 0.099 | 30 | 0.134 | 0.099 | 30 |  |  |  | 0.1 | 0.3
2008-01-23 | [18 empty] | 0.1 | 0.3
2008-01-24 | 0.179 | 0.168 | 25 | 0.216 | 0.183 | 30 | 0.127 | 0.094 | 12 | 0.179 | 0.168 | 25 | 0.216 | 0.183 | 30 | 0.127 | 0.094 | 12 | 0.1 | 0.3
2008-01-25 | [18 empty] | 0.1 | 0.3
2008-01-26 | [18 empty] | 0.1 | 0.3
2008-01-27 | 0.078 | 0.071 | 14 | 0.088 | 0.084 | 15 | 0.082 | 0.079 | 13 | 0.078 | 0.071 | 14 | 0.088 | 0.084 | 15 | 0.082 | 0.079 | 13 | 0.1 | 0.3
2008-01-28 | [6 empty] | 0.143 | 0.065 | 12 | [6 empty] | 0.143 | 0.065 | 12 | 0.1 | 0.3
2008-01-29 | [18 empty] | 0.1 | 0.3
2008-01-30 | 0.075 | 0.066 | 17 | 0.106 | 0.092 | 17 |  |  |  | 0.075 | 0.066 | 17 | 0.106 | 0.092 | 17 |  |  |  | 0.1 | 0.3
2008-01-31 | [6 empty] | 0.07 | 0.055 | 15 | [6 empty] | 0.07 | 0.055 | 15 | 0.1 | 0.3
2008-02-01 |  |  |  | 0.094 | 0.088 | 15 | [6 empty] | 0.094 | 0.088 | 15 |  |  |  | 0.1 | 0.3
2008-02-02 | 0.071 | 0.07 | 14 | [6 empty] | 0.071 | 0.07 | 14 | [6 empty] | 0.1 | 0.3
2008-02-03 | [6 empty] | 0.085 | 0.064 | 11 | [6 empty] | 0.085 | 0.064 | 11 | 0.1 | 0.3
2008-02-04 |  |  |  | 0.572 | 0.055 | 8 | [6 empty] | 0.572 | 0.055 | 8 |  |  |  | 0.1 | 0.3
2008-02-05 | [6 empty] | 0.066 | 0.063 | 11 | [6 empty] | 0.066 | 0.063 | 11 | 0.1 | 0.3
2008-02-06 | [18 empty] | 0.1 | 0.3
2008-02-07 | 0.115 | 0.111 | 50 | 0.801 | 0.266 | 320 | 0.424 | 0.24 | 140 | 0.115 | 0.111 | 50 | 0.801 | 0.266 | 320 | 0.424 | 0.24 | 140 | 0.1 | 0.3
2008-02-08 | 0.742 | 0.105 | 30 | [6 empty] | 0.742 | 0.105 | 30 | [6 empty] | 0.1 | 0.3
2008-02-09 |  |  |  | 0.144 | 0.088 | 25 | 0.064 | 0.061 | 12 |  |  |  | 0.144 | 0.088 | 25 | 0.064 | 0.061 | 12 | 0.1 | 0.3
2008-02-10 | [18 empty] | 0.1 | 0.3
2008-02-11 | [18 empty] | 0.1 | 0.3
2008-02-12 | [18 empty] | 0.1 | 0.3
2008-02-13 | 0.1 | 0.091 | 22 | [6 empty] | 0.1 | 0.091 | 22 | [6 empty] | 0.1 | 0.3
2008-02-14 |  |  |  | 0.119 | 0.09 | 25 | 0.08 | 0.059 | 16 |  |  |  | 0.119 | 0.09 | 25 | 0.08 | 0.059 | 16 | 0.1 | 0.3
2008-02-15 | 0.125 | 0.1 | 30 |  |  |  | 0.074 | 0.07 | 13 | 0.125 | 0.1 | 30 |  |  |  | 0.074 | 0.07 | 13 | 0.1 | 0.3
2008-02-16 |  |  |  | 0.125 | 0.097 | 30 | 0.078 | 0.063 | 10 |  |  |  | 0.125 | 0.097 | 30 | 0.078 | 0.063 | 10 | 0.1 | 0.3
2008-02-17 | 0.127 | 0.096 | 35 | [6 empty] | 0.127 | 0.096 | 35 | [6 empty] | 0.1 | 0.3
2008-02-18 |  |  |  | 0.115 | 0.098 | 10 | 0.069 | 0.066 | 10 |  |  |  | 0.115 | 0.098 | 10 | 0.069 | 0.066 | 10 | 0.1 | 0.3
2008-02-19 |  | 0.149 | 150 | [7 empty] | 0.149 | 150 | [6 empty] | 0.1 | 0.3
2008-02-20 |  |  |  | 0.442 | 0.162 | 155 | 0.121 | 0.081 | 15 |  |  |  | 0.442 | 0.162 | 155 | 0.121 | 0.081 | 15 | 0.1 | 0.3
2008-02-21 | 0.12 | 0.108 | 25 | [6 empty] | 0.12 | 0.108 | 25 | [6 empty] | 0.1 | 0.3
2008-02-22 |  |  |  | 0.115 | 0.104 | 20 | 0.074 | 0.073 | 13 |  |  |  | 0.115 | 0.104 | 20 | 0.074 | 0.073 | 13 | 0.1 | 0.3
2008-02-23 | 0.153 | 0.124 | 30 | [6 empty] | 0.153 | 0.124 | 30 | [6 empty] | 0.1 | 0.3
2008-02-24 |  |  |  | 0.155 | 0.099 | 30 | [6 empty] | 0.155 | 0.099 | 30 |  |  |  | 0.1 | 0.3
2008-02-25 | 0.134 | 0.109 | 30 |  |  |  | 0.075 | 0.073 | 13 | 0.134 | 0.109 | 30 |  |  |  | 0.075 | 0.073 | 13 | 0.1 | 0.3
2008-02-26 |  |  |  | 0.14 | 0.099 | 30 | [6 empty] | 0.14 | 0.099 | 30 |  |  |  | 0.1 | 0.3
2008-02-27 | 0.127 | 0.12 | 25 |  |  |  | 0.075 | 0.073 | 13 | 0.127 | 0.12 | 25 |  |  |  | 0.075 | 0.073 | 13 | 0.1 | 0.3
2008-02-28 | [18 empty] | 0.1 | 0.3
2008-02-29 | [18 empty] | 0.1 | 0.3
2008-03-01 | [18 empty] | 0.1 | 0.3
2008-03-02 | [18 empty] | 0.1 | 0.3
2008-03-03 | [18 empty] | 0.1 | 0.3
2008-03-04 | [18 empty] | 0.1 | 0.3
2008-03-05 | [18 empty] | 0.1 | 0.3
2008-03-06 | [18 empty] | 0.1 | 0.3
2008-03-07 | [18 empty] | 0.1 | 0.3
2008-03-08 | [18 empty] | 0.1 | 0.3
2008-03-09 | [18 empty] | 0.1 | 0.3
2008-03-10 | [18 empty] | 0.1 | 0.3
2008-03-11 | [18 empty] | 0.1 | 0.3
2008-03-12 | [18 empty] | 0.1 | 0.3
2008-03-13 | [18 empty] | 0.1 | 0.3
2008-03-14 | [18 empty] | 0.1 | 0.3
2008-03-15 | [18 empty] | 0.1 | 0.3
2008-03-16 | [18 empty] | 0.1 | 0.3
2008-03-17 | [18 empty] | 0.1 | 0.3
2008-03-18 | [18 empty] | 0.1 | 0.3
2008-03-19 | [18 empty] | 0.1 | 0.3
2008-03-20 | [18 empty] | 0.1 | 0.3
2008-03-21 | [18 empty] | 0.1 | 0.3
2008-03-22 | [18 empty] | 0.1 | 0.3
2008-03-23 | [18 empty] | 0.1 | 0.3
2008-03-24 | [18 empty] | 0.1 | 0.3
2008-03-25 | [18 empty] | 0.1 | 0.3
2008-03-26 | [18 empty] | 0.1 | 0.3
2008-03-27 | [18 empty] | 0.1 | 0.3
2008-03-28 | [18 empty] | 0.1 | 0.3
2008-03-29 | [18 empty] | 0.1 | 0.3
2008-03-30 | [18 empty] | 0.1 | 0.3
2008-03-31 | [18 empty] | 0.1 | 0.3
2008-04-01 | [18 empty] | 0.1 | 0.3
2008-04-02 | [18 empty] | 0.1 | 0.3
2008-04-03 | 0.081 | 0.075 | 16 |  |  |  | 0.082 | 0.06 | 13 | 0.081 | 0.075 | 16 |  |  |  | 0.082 | 0.06 | 13 | 0.1 | 0.3
2008-04-04 |  |  |  | 0.113 | 0.066 | 17 | [6 empty] | 0.113 | 0.066 | 17 |  |  |  | 0.1 | 0.3
2008-04-05 | [6 empty] | 0.158 | 0.074 | 12 | [6 empty] | 0.158 | 0.074 | 12 | 0.1 | 0.3
2008-04-06 | 0.095 | 0.087 | 12 | 0.074 | 0.071 | 11 |  |  |  | 0.095 | 0.087 | 12 | 0.074 | 0.071 | 11 |  |  |  | 0.1 | 0.3
2008-04-07 | [18 empty] | 0.1 | 0.3
2008-04-08 | [18 empty] | 0.1 | 0.3
2008-04-09 | [6 empty] | 0.141 | 0.08 | 15 | [6 empty] | 0.141 | 0.08 | 15 | 0.1 | 0.3
2008-04-10 | 0.144 | 0.099 | 16 | 0.079 | 0.071 | 12 |  |  |  | 0.144 | 0.099 | 16 | 0.079 | 0.071 | 12 |  |  |  | 0.1 | 0.3
2008-04-11 | [18 empty] | 0.1 | 0.3
2008-04-12 | [18 empty] | 0.1 | 0.3
2008-04-13 | [18 empty] | 0.1 | 0.3
2008-04-14 | [18 empty] | 0.1 | 0.3
2008-04-15 | [18 empty] | 0.1 | 0.3
2008-04-16 | [18 empty] | 0.1 | 0.3
2008-04-17 | [18 empty] | 0.1 | 0.3
2008-04-18 | [18 empty] | 0.1 | 0.3
2008-04-19 | [18 empty] | 0.1 | 0.3
2008-04-20 | [18 empty] | 0.1 | 0.3
2008-04-21 | [18 empty] | 0.1 | 0.3
2008-04-22 | [18 empty] | 0.1 | 0.3
2008-04-23 | [18 empty] | 0.1 | 0.3
2008-04-24 | [18 empty] | 0.1 | 0.3
2008-04-25 | [18 empty] | 0.1 | 0.3
2008-04-26 | 0.165 | 0.092 | 11 | [6 empty] | 0.165 | 0.092 | 11 | [6 empty] | 0.1 | 0.3
2008-04-27 | [6 empty] | 0.108 | 0.072 | 12 | [6 empty] | 0.108 | 0.072 | 12 | 0.1 | 0.3
2008-04-28 |  |  |  | 0.067 | 0.063 | 14 | [6 empty] | 0.067 | 0.063 | 14 |  |  |  | 0.1 | 0.3
2008-04-29 | [18 empty] | 0.1 | 0.3
2008-04-30 | 0.122 | 0.074 | 13 | [6 empty] | 0.122 | 0.074 | 13 | [6 empty] | 0.1 | 0.3
2008-05-01 |  |  |  | 0.059 | 0.054 | 14 | [6 empty] | 0.059 | 0.054 | 14 |  |  |  | 0.1 | 0.3
2008-05-02 | [18 empty] | 0.1 | 0.3
2008-05-03 | 0.079 | 0.072 | 13 | [6 empty] | 0.079 | 0.072 | 13 | [6 empty] | 0.1 | 0.3
2008-05-04 |  |  |  | 0.059 | 0.049 | 12 | [6 empty] | 0.059 | 0.049 | 12 |  |  |  | 0.1 | 0.3
2008-05-05 | [6 empty] | 0.096 | 0.084 | 10 | [6 empty] | 0.096 | 0.084 | 10 | 0.1 | 0.3
2008-05-06 | [18 empty] | 0.1 | 0.3
2008-05-07 | 0.076 | 0.069 | 13 | 0.056 | 0.031 | 9 |  |  |  | 0.076 | 0.069 | 13 | 0.056 | 0.031 | 9 |  |  |  | 0.1 | 0.3
2008-05-08 | [18 empty] | 0.1 | 0.3
2008-05-09 | [18 empty] | 0.1 | 0.3
2008-05-10 | 0.083 | 0.076 | 11 | [6 empty] | 0.083 | 0.076 | 11 | [6 empty] | 0.1 | 0.3
2008-05-11 |  |  |  | 0.062 | 0.058 | 13 | [6 empty] | 0.062 | 0.058 | 13 |  |  |  | 0.1 | 0.3
2008-05-12 | [6 empty] | 0.146 | 0.066 | 14 | [6 empty] | 0.146 | 0.066 | 14 | 0.1 | 0.3
2008-05-13 | [18 empty] | 0.1 | 0.3
2008-05-14 | 0.149 | 0.088 | 12 | [6 empty] | 0.149 | 0.088 | 12 | [6 empty] | 0.1 | 0.3
2008-05-15 |  |  |  | 0.12 | 0.074 | 12 | 0.236 | 0.07 | 13 |  |  |  | 0.12 | 0.074 | 12 | 0.236 | 0.07 | 13 | 0.1 | 0.3
2008-05-16 | [18 empty] | 0.1 | 0.3
2008-05-17 | 0.184 | 0.08 | 17 | [6 empty] | 0.184 | 0.08 | 17 | [6 empty] | 0.1 | 0.3
2008-05-18 |  |  |  | 0.116 | 0.066 | 15 | 0.228 | 0.063 | 20 |  |  |  | 0.116 | 0.066 | 15 | 0.228 | 0.063 | 20 | 0.1 | 0.3
2008-05-19 | 0.325 | 0.086 | 12 | 0.067 | 0.059 | 12 | 0.129 | 0.063 | 20 | 0.325 | 0.086 | 12 | 0.067 | 0.059 | 12 | 0.129 | 0.063 | 20 | 0.1 | 0.3
2008-05-20 | [18 empty] | 0.1 | 0.3
2008-05-21 | 0.148 | 0.098 | 11 | [6 empty] | 0.148 | 0.098 | 11 | [6 empty] | 0.1 | 0.3
2008-05-22 |  |  |  | 0.099 | 0.058 | 20 | [6 empty] | 0.099 | 0.058 | 20 |  |  |  | 0.1 | 0.3
2008-05-23 | [6 empty] | 0.164 | 0.094 | 21 | [6 empty] | 0.164 | 0.094 | 21 | 0.1 | 0.3
2008-05-24 | 0.112 | 0.087 | 11 | [6 empty] | 0.112 | 0.087 | 11 | [6 empty] | 0.1 | 0.3
2008-05-25 |  |  |  | 0.09 | 0.081 | 11 | [6 empty] | 0.09 | 0.081 | 11 |  |  |  | 0.1 | 0.3
2008-05-26 | [18 empty] | 0.1 | 0.3
2008-05-27 | 0.118 | 0.095 | 12 | [6 empty] | 0.118 | 0.095 | 12 | [6 empty] | 0.1 | 0.3
2008-05-28 |  |  |  | 0.097 | 0.075 | 12 | [6 empty] | 0.097 | 0.075 | 12 |  |  |  | 0.1 | 0.3
2008-05-29 | 0.105 | 0.083 | 11 | [6 empty] | 0.105 | 0.083 | 11 | [6 empty] | 0.1 | 0.3
2008-05-30 | [18 empty] | 0.1 | 0.3
2008-05-31 |  |  |  | 0.124 | 0.076 | 13 | 0.156 | 0.089 | 30 |  |  |  | 0.124 | 0.076 | 13 | 0.156 | 0.089 | 30 | 0.1 | 0.3
2008-06-01 | 0.125 | 0.096 | 13 | [6 empty] | 0.125 | 0.096 | 13 | [6 empty] | 0.1 | 0.3
2008-06-02 | [18 empty] | 0.1 | 0.3
2008-06-03 | 0.154 | 0.098 | 19 | 0.125 | 0.089 | 17 |  |  |  | 0.154 | 0.098 | 19 | 0.125 | 0.089 | 17 |  |  |  | 0.1 | 0.3
2008-06-04 | 0.202 | 0.092 | 20 | 0.261 | 0.091 | 20 |  |  |  | 0.202 | 0.092 | 20 | 0.261 | 0.091 | 20 |  |  |  | 0.1 | 0.3
2008-06-05 | [6 empty] | 0.108 | 0.145 | 20 | [6 empty] | 0.108 | 0.145 | 20 | 0.1 | 0.3
2008-06-06 | 0.137 | 0.099 | 17 | 0.139 | 0.109 | 30 |  |  |  | 0.137 | 0.099 | 17 | 0.139 | 0.109 | 30 |  |  |  | 0.1 | 0.3
2008-06-07 | 0.151 | 0.095 | 16 | 0.124 | 0.099 | 21 | 0.201 | 0.095 | 25 | 0.151 | 0.095 | 16 | 0.124 | 0.099 | 21 | 0.201 | 0.095 | 25 | 0.1 | 0.3
2008-06-08 | [18 empty] | 0.1 | 0.3
2008-06-09 | [18 empty] | 0.1 | 0.3
2008-06-10 | [18 empty] | 0.1 | 0.3
2008-06-11 | [18 empty] | 0.1 | 0.3
2008-06-12 | [18 empty] | 0.1 | 0.3
2008-06-13 | [18 empty] | 0.1 | 0.3
2008-06-14 | [18 empty] | 0.1 | 0.3
2008-06-15 | [18 empty] | 0.1 | 0.3
2008-06-16 | [18 empty] | 0.1 | 0.3
2008-06-17 | [18 empty] | 0.1 | 0.3
2008-06-18 | [18 empty] | 0.1 | 0.3
2008-06-19 | [18 empty] | 0.1 | 0.3
2008-06-20 | [18 empty] | 0.1 | 0.3
2008-06-21 | [18 empty] | 0.1 | 0.3
2008-06-22 | [18 empty] | 0.1 | 0.3
2008-06-23 | [18 empty] | 0.1 | 0.3
2008-06-24 | [18 empty] | 0.1 | 0.3
2008-06-25 | [18 empty] | 0.1 | 0.3
2008-06-26 | [18 empty] | 0.1 | 0.3
2008-06-27 | [18 empty] | 0.1 | 0.3
2008-06-28 | [18 empty] | 0.1 | 0.3
2008-06-29 | 0.113 | 0.087 | 13 | 0.118 | 0.096 | 17 |  |  |  | 0.113 | 0.087 | 13 | 0.118 | 0.096 | 17 |  |  |  | 0.1 | 0.3
2008-06-30 | 0.111 | 0.092 | 12 | 0.095 | 0.088 | 10 | 0.185 | 0.093 | 25 | 0.111 | 0.092 | 12 | 0.095 | 0.088 | 10 | 0.185 | 0.093 | 25 | 0.1 | 0.3
2008-07-01 | [18 empty] | 0.1 | 0.3
2008-07-02 | 0.131 | 0.117 | 30 | [6 empty] | 0.131 | 0.117 | 30 | [6 empty] | 0.1 | 0.3
2008-07-03 |  |  |  | 0.072 | 0.066 | 22 | 0.154 | 0.085 | 23 |  |  |  | 0.072 | 0.066 | 22 | 0.154 | 0.085 | 23 | 0.1 | 0.3
2008-07-04 | [18 empty] | 0.1 | 0.3
2008-07-05 | 0.126 | 0.092 | 15 | [6 empty] | 0.126 | 0.092 | 15 | [6 empty] | 0.1 | 0.3
2008-07-06 |  |  |  | 0.104 | 0.085 | 10 | 0.208 | 0.095 | 25 |  |  |  | 0.104 | 0.085 | 10 | 0.208 | 0.095 | 25 | 0.1 | 0.3
2008-07-07 | 0.142 | 0.07 | 20 | [6 empty] | 0.142 | 0.07 | 20 | [6 empty] | 0.1 | 0.3
2008-07-08 | 0.12 | 0.073 | 16 | [6 empty] | 0.12 | 0.073 | 16 | [6 empty] | 0.1 | 0.3
2008-07-09 | [6 empty] | 0.17 | 0.094 | 22 | [6 empty] | 0.17 | 0.094 | 22 | 0.1 | 0.3
2008-07-10 | 0.106 | 0.073 | 16 | 0.131 | 0.103 | 25 |  |  |  | 0.106 | 0.073 | 16 | 0.131 | 0.103 | 25 |  |  |  | 0.1 | 0.3
2008-07-11 | 0.135 | 0.084 | 14 |  |  |  | 0.237 | 0.09 | 21 | 0.135 | 0.084 | 14 |  |  |  | 0.237 | 0.09 | 21 | 0.1 | 0.3
2008-07-12 | [18 empty] | 0.1 | 0.3
2008-07-13 | 0.127 | 0.087 | 11 | 0.112 | 0.055 | 15 | 0.167 | 0.092 | 18 | 0.127 | 0.087 | 11 | 0.112 | 0.055 | 15 | 0.167 | 0.092 | 18 | 0.1 | 0.3
2008-07-14 | 0.126 | 0.086 | 12 | [6 empty] | 0.126 | 0.086 | 12 | [6 empty] | 0.1 | 0.3
2008-07-15 | 0.135 | 0.095 | 13 | 0.148 | 0.088 | 11 | 0.16 | 0.088 | 18 | 0.135 | 0.095 | 13 | 0.148 | 0.088 | 11 | 0.16 | 0.088 | 18 | 0.1 | 0.3
2008-07-16 | 0.637 | 0.115 | 52 | 0.701 | 0.17 | 92 |  |  |  | 0.637 | 0.115 | 52 | 0.701 | 0.17 | 92 |  |  |  | 0.1 | 0.3
2008-07-17 | [6 empty] | 0.166 | 0.094 | 22 | [6 empty] | 0.166 | 0.094 | 22 | 0.1 | 0.3
2008-07-18 | 0.18 | 0.093 | 19 | [6 empty] | 0.18 | 0.093 | 19 | [6 empty] | 0.1 | 0.3
2008-07-19 |  |  |  | 0.211 | 0.088 | 16 | [6 empty] | 0.211 | 0.088 | 16 |  |  |  | 0.1 | 0.3
2008-07-20 | 0.21 | 0.098 | 25 |  |  |  | 0.198 | 0.077 | 22 | 0.21 | 0.098 | 25 |  |  |  | 0.198 | 0.077 | 22 | 0.1 | 0.3
2008-07-21 | 0.187 | 0.094 | 17 | 0.15 | 0.063 | 17 |  |  |  | 0.187 | 0.094 | 17 | 0.15 | 0.063 | 17 |  |  |  | 0.1 | 0.3
2008-07-22 | [18 empty] | 0.1 | 0.3
2008-07-23 | 0.199 | 0.092 | 19 |  |  |  | 0.236 | 0.086 | 30 | 0.199 | 0.092 | 19 |  |  |  | 0.236 | 0.086 | 30 | 0.1 | 0.3
2008-07-24 | 0.201 | 0.099 | 27 | 0.152 | 0.068 | 15 |  |  |  | 0.201 | 0.099 | 27 | 0.152 | 0.068 | 15 |  |  |  | 0.1 | 0.3
2008-07-25 | 0.236 | 0.098 | 26 | 0.169 | 0.078 | 15 | 0.213 | 0.09 | 20 | 0.236 | 0.098 | 26 | 0.169 | 0.078 | 15 | 0.213 | 0.09 | 20 | 0.1 | 0.3
2008-07-26 | [18 empty] | 0.1 | 0.3
2008-07-27 | 0.227 | 0.108 | 35 | 0.156 | 0.09 | 15 |  |  |  | 0.227 | 0.108 | 35 | 0.156 | 0.09 | 15 |  |  |  | 0.1 | 0.3
2008-07-28 | 0.185 | 0.106 | 36 |  |  |  | 0.185 | 0.088 | 21 | 0.185 | 0.106 | 36 |  |  |  | 0.185 | 0.088 | 21 | 0.1 | 0.3
2008-07-29 | 0.202 | 0.117 | 45 | 0.184 | 0.098 | 26 |  |  |  | 0.202 | 0.117 | 45 | 0.184 | 0.098 | 26 |  |  |  | 0.1 | 0.3
2008-07-30 | [18 empty] | 0.1 | 0.3
2008-07-31 | 0.227 | 0.108 | 35 | 0.156 | 0.09 | 15 |  |  |  | 0.227 | 0.108 | 35 | 0.156 | 0.09 | 15 |  |  |  | 0.1 | 0.3
2008-08-01 |  |  |  | 0.205 | 0.085 | 20 | [6 empty] | 0.205 | 0.085 | 20 |  |  |  | 0.1 | 0.3
2008-08-02 | [18 empty] | 0.1 | 0.3
2008-08-03 | 0.242 | 0.09 | 27 | 0.23 | 0.092 | 19 | 0.356 | 0.09 | 33 | 0.242 | 0.09 | 27 | 0.23 | 0.092 | 19 | 0.356 | 0.09 | 33 | 0.1 | 0.3
2008-08-04 | [18 empty] | 0.1 | 0.3
2008-08-05 | [6 empty] | 0.251 | 0.09 | 25 | [6 empty] | 0.251 | 0.09 | 25 | 0.1 | 0.3
2008-08-06 | 0.234 | 0.103 | 45 | [6 empty] | 0.234 | 0.103 | 45 | [6 empty] | 0.1 | 0.3
2008-08-07 |  |  |  | 0.189 | 0.088 | 20 | 0.229 | 0.083 | 19 |  |  |  | 0.189 | 0.088 | 20 | 0.229 | 0.083 | 19 | 0.1 | 0.3
2008-08-08 | 0.243 | 0.104 | 30 |  |  |  | 0.189 | 0.089 | 20 | 0.243 | 0.104 | 30 |  |  |  | 0.189 | 0.089 | 20 | 0.1 | 0.3
2008-08-09 | [18 empty] | 0.1 | 0.3
2008-08-10 | 0.213 | 0.098 | 23 | 0.209 | 0.094 | 16 | 0.187 | 0.086 | 25 | 0.213 | 0.098 | 23 | 0.209 | 0.094 | 16 | 0.187 | 0.086 | 25 | 0.1 | 0.3
2008-08-11 | [18 empty] | 0.1 | 0.3
2008-08-12 | [18 empty] | 0.1 | 0.3
2008-08-13 | 0.159 | 0.096 | 17 | 0.15 | 0.088 | 14 | 0.18 | 0.091 | 27 | 0.159 | 0.096 | 17 | 0.15 | 0.088 | 14 | 0.18 | 0.091 | 27 | 0.1 | 0.3
2008-08-14 | [18 empty] | 0.1 | 0.3
2008-08-15 | 0.202 | 0.091 | 20 |  |  |  | 0.238 | 0.09 | 25 | 0.202 | 0.091 | 20 |  |  |  | 0.238 | 0.09 | 25 | 0.1 | 0.3
2008-08-16 |  |  |  | 0.16 | 0.086 | 17 | [6 empty] | 0.16 | 0.086 | 17 |  |  |  | 0.1 | 0.3
2008-08-17 | [6 empty] | 0.198 | 0.091 | 25 | [6 empty] | 0.198 | 0.091 | 25 | 0.1 | 0.3
2008-08-18 | 0.201 | 0.097 | 30 | [6 empty] | 0.201 | 0.097 | 30 | [6 empty] | 0.1 | 0.3
2008-08-19 | [6 empty] | 0.223 | 0.085 | 30 | [6 empty] | 0.223 | 0.085 | 30 | 0.1 | 0.3
2008-08-20 | 0.182 | 0.097 | 25 | 0.145 | 0.086 | 15 |  |  |  | 0.182 | 0.097 | 25 | 0.145 | 0.086 | 15 |  |  |  | 0.1 | 0.3
2008-08-21 | [18 empty] | 0.1 | 0.3
2008-08-22 | [18 empty] | 0.1 | 0.3
2008-08-23 | 0.212 | 0.098 | 23 | 0.183 | 0.092 | 20 |  |  |  | 0.212 | 0.098 | 23 | 0.183 | 0.092 | 20 |  |  |  | 0.1 | 0.3
2008-08-24 | 0.184 | 0.088 | 20 | [6 empty] | 0.184 | 0.088 | 20 | [6 empty] | 0.1 | 0.3
2008-08-25 |  |  |  | 0.163 | 0.078 | 14 | 0.175 | 0.068 | 26 |  |  |  | 0.163 | 0.078 | 14 | 0.175 | 0.068 | 26 | 0.1 | 0.3
2008-08-26 | 0.181 | 0.07 | 30 | [6 empty] | 0.181 | 0.07 | 30 | [6 empty] | 0.1 | 0.3
2008-08-27 | [6 empty] | 0.17 | 0.096 | 20 | [6 empty] | 0.17 | 0.096 | 20 | 0.1 | 0.3
2008-08-28 |  |  |  | 0.145 | 0.058 | 20 | [6 empty] | 0.145 | 0.058 | 20 |  |  |  | 0.1 | 0.3
2008-08-29 | 0.184 | 0.097 | 21 | [6 empty] | 0.184 | 0.097 | 21 | [6 empty] | 0.1 | 0.3
2008-08-30 |  |  |  | 0.189 | 0.085 | 18 | [6 empty] | 0.189 | 0.085 | 18 |  |  |  | 0.1 | 0.3
2008-08-31 | [6 empty] | 0.238 | 0.09 | 35 | [6 empty] | 0.238 | 0.09 | 35 | 0.1 | 0.3
2008-09-01 | [18 empty] | 0.1 | 0.3
2008-09-02 | [18 empty] | 0.1 | 0.3
2008-09-03 | [6 empty] | 0.37 | 0.112 | 45 | [6 empty] | 0.37 | 0.112 | 45 | 0.1 | 0.3
2008-09-04 | [18 empty] | 0.1 | 0.3
2008-09-05 |  |  |  | 0.22 | 0.099 | 37 | [6 empty] | 0.22 | 0.099 | 37 |  |  |  | 0.1 | 0.3
2008-09-06 | 0.23 | 0.097 | 27 | [6 empty] | 0.23 | 0.097 | 27 | [6 empty] | 0.1 | 0.3
2008-09-07 | 0.236 | 0.099 | 61 |  |  |  | 0.254 | 0.088 | 35 | 0.236 | 0.099 | 61 |  |  |  | 0.254 | 0.088 | 35 | 0.1 | 0.3
2008-09-08 | 0.441 | 0.137 | 159 | 0.193 | 0.137 | 40 |  |  |  | 0.441 | 0.137 | 159 | 0.193 | 0.137 | 40 |  |  |  | 0.1 | 0.3
2008-09-09 | [6 empty] | 0.324 | 0.119 | 45 | [6 empty] | 0.324 | 0.119 | 45 | 0.1 | 0.3
2008-09-10 | [18 empty] | 0.1 | 0.3
2008-09-11 | [18 empty] | 0.1 | 0.3
2008-09-12 | 0.184 | 0.097 | 37 | 0.126 | 0.081 | 24 |  |  |  | 0.184 | 0.097 | 37 | 0.126 | 0.081 | 24 |  |  |  | 0.1 | 0.3
2008-09-13 | [6 empty] | 0.211 | 0.124 | 30 | [6 empty] | 0.211 | 0.124 | 30 | 0.1 | 0.3
2008-09-14 | [18 empty] | 0.1 | 0.3
2008-09-15 | [18 empty] | 0.1 | 0.3
2008-09-16 | [6 empty] | 0.323 | 0.13 | 40 | [6 empty] | 0.323 | 0.13 | 40 | 0.1 | 0.3
2008-09-17 | 0.236 | 0.099 | 35 | 0.146 | 0.098 | 23 |  |  |  | 0.236 | 0.099 | 35 | 0.146 | 0.098 | 23 |  |  |  | 0.1 | 0.3
2008-09-18 | [18 empty] | 0.1 | 0.3
2008-09-19 | [18 empty] | 0.1 | 0.3
2008-09-20 | [6 empty] | 0.268 | 0.097 | 35 | [6 empty] | 0.268 | 0.097 | 35 | 0.1 | 0.3
2008-09-21 | 0.271 | 0.139 | 30 | 0.157 | 0.112 | 38 | 0.038 | 0.038 | 20 | 0.271 | 0.139 | 30 | 0.157 | 0.112 | 38 | 0.038 | 0.038 | 20 | 0.1 | 0.3
2008-09-22 | [18 empty] | 0.1 | 0.3
2008-09-23 | [18 empty] | 0.1 | 0.3
2008-09-24 | 0.355 | 0.152 | 35 | 0.167 | 0.147 | 30 | 0.264 | 0.098 | 43 | 0.355 | 0.152 | 35 | 0.167 | 0.147 | 30 | 0.264 | 0.098 | 43 | 0.1 | 0.3
2008-09-25 | [18 empty] | 0.1 | 0.3
2008-09-26 | [18 empty] | 0.1 | 0.3
2008-09-27 | 0.264 | 0.172 | 30 |  |  |  | 0.207 | 0.117 | 30 | 0.264 | 0.172 | 30 |  |  |  | 0.207 | 0.117 | 30 | 0.1 | 0.3
2008-09-28 |  |  |  | 0.169 | 0.115 | 30 | [6 empty] | 0.169 | 0.115 | 30 |  |  |  | 0.1 | 0.3
2008-09-29 | [18 empty] | 0.1 | 0.3
2008-09-30 | [18 empty] | 0.1 | 0.3
2008-10-01 | [6 empty] | 0.193 | 0.11 | 30 | [6 empty] | 0.193 | 0.11 | 30 | 0.1 | 0.3
2008-10-02 | 0.244 | 0.145 | 30 | 0.149 | 0.099 | 30 |  |  |  | 0.244 | 0.145 | 30 | 0.149 | 0.099 | 30 |  |  |  | 0.1 | 0.3
2008-10-03 | [18 empty] | 0.1 | 0.3
2008-10-04 | [6 empty] | 0.183 | 0.092 | 29 | [6 empty] | 0.183 | 0.092 | 29 | 0.1 | 0.3
2008-10-05 | 0.254 | 0.138 | 32 | 0.149 | 0.109 | 28 |  |  |  | 0.254 | 0.138 | 32 | 0.149 | 0.109 | 28 |  |  |  | 0.1 | 0.3
2008-10-06 |  |  |  | 0.115 | 0.119 | 28 | [6 empty] | 0.115 | 0.119 | 28 |  |  |  | 0.1 | 0.3
2008-10-07 | [6 empty] | 0.207 | 0.097 | 30 | [6 empty] | 0.207 | 0.097 | 30 | 0.1 | 0.3
2008-10-08 | [18 empty] | 0.1 | 0.3
2008-10-09 | [18 empty] | 0.1 | 0.3
2008-10-10 | 0.179 | 0.126 | 25 |  |  |  | 0.244 | 0.1 | 30 | 0.179 | 0.126 | 25 |  |  |  | 0.244 | 0.1 | 30 | 0.1 | 0.3
2008-10-11 | [18 empty] | 0.1 | 0.3
2008-10-12 |  |  |  | 0.172 | 0.109 | 30 | 0.195 | 0.102 | 25 |  |  |  | 0.172 | 0.109 | 30 | 0.195 | 0.102 | 25 | 0.1 | 0.3
2008-10-13 | [6 empty] | 0.198 | 0.081 | 30 | [6 empty] | 0.198 | 0.081 | 30 | 0.1 | 0.3
2008-10-14 | [18 empty] | 0.1 | 0.3
2008-10-15 | [6 empty] | 0.187 | 0.095 | 30 | [6 empty] | 0.187 | 0.095 | 30 | 0.1 | 0.3
2008-10-16 | [18 empty] | 0.1 | 0.3
2008-10-17 | [6 empty] | 0.221 | 0.088 | 30 | [6 empty] | 0.221 | 0.088 | 30 | 0.1 | 0.3
2008-10-18 | [6 empty] | 0.177 | 0.085 | 29 | [6 empty] | 0.177 | 0.085 | 29 | 0.1 | 0.3
2008-10-19 | 0.247 | 0.139 | 32 | [6 empty] | 0.247 | 0.139 | 32 | [6 empty] | 0.1 | 0.3
2008-10-20 |  |  |  | 0.273 | 0.223 | 38 | 0.249 | 0.102 | 23 |  |  |  | 0.273 | 0.223 | 38 | 0.249 | 0.102 | 23 | 0.1 | 0.3
2008-10-21 | [18 empty] | 0.1 | 0.3
2008-10-22 | 0.245 | 0.192 | 30 | 0.207 | 0.199 | 30 | 0.17 | 0.097 | 30 | 0.245 | 0.192 | 30 | 0.207 | 0.199 | 30 | 0.17 | 0.097 | 30 | 0.1 | 0.3
2008-10-23 | [18 empty] | 0.1 | 0.3
2008-10-24 | [18 empty] | 0.1 | 0.3
2008-10-25 | 0.161 | 0.144 | 31 | 0.13 | 0.099 | 29 | 0.164 | 0.091 | 24 | 0.161 | 0.144 | 31 | 0.13 | 0.099 | 29 | 0.164 | 0.091 | 24 | 0.1 | 0.3
2008-10-26 | [18 empty] | 0.1 | 0.3
2008-10-27 | [6 empty] | 0.441 | 0.138 | 28 | [6 empty] | 0.441 | 0.138 | 28 | 0.1 | 0.3
2008-10-28 | [18 empty] | 0.1 | 0.3
2008-10-29 |  |  |  | 0.078 | 0.076 | 15 | [6 empty] | 0.078 | 0.076 | 15 |  |  |  | 0.1 | 0.3
2008-10-30 | 0.15 | 0.064 | 12 |  |  |  | 0.151 | 0.093 | 32 | 0.15 | 0.064 | 12 |  |  |  | 0.151 | 0.093 | 32 | 0.1 | 0.3
2008-10-31 | [18 empty] | 0.1 | 0.3
2008-11-01 |  |  |  | 0.127 | 0.086 | 12 | [6 empty] | 0.127 | 0.086 | 12 |  |  |  | 0.1 | 0.3
2008-11-02 | 0.226 | 0.164 | 30 |  |  |  | 0.127 | 0.096 | 25 | 0.226 | 0.164 | 30 |  |  |  | 0.127 | 0.096 | 25 | 0.1 | 0.3
2008-11-03 |  |  |  | 0.241 | 0.13 | 30 | [6 empty] | 0.241 | 0.13 | 30 |  |  |  | 0.1 | 0.3
2008-11-04 | 0.178 | 0.131 | 12 | [6 empty] | 0.178 | 0.131 | 12 | [6 empty] | 0.1 | 0.3
2008-11-05 | [6 empty] | 0.127 | 0.109 | 20 | [6 empty] | 0.127 | 0.109 | 20 | 0.1 | 0.3
2008-11-06 |  |  |  | 0.161 | 0.117 | 21 | [6 empty] | 0.161 | 0.117 | 21 |  |  |  | 0.1 | 0.3
2008-11-07 | 0.155 | 0.09 | 18 | [6 empty] | 0.155 | 0.09 | 18 | [6 empty] | 0.1 | 0.3
2008-11-08 | [6 empty] | 0.116 | 0.098 | 20 | [6 empty] | 0.116 | 0.098 | 20 | 0.1 | 0.3
2008-11-09 |  |  |  | 0.144 | 0.085 | 20 | [6 empty] | 0.144 | 0.085 | 20 |  |  |  | 0.1 | 0.3
2008-11-10 | 0.166 | 0.086 | 22 | [6 empty] | 0.166 | 0.086 | 22 | [6 empty] | 0.1 | 0.3
2008-11-11 | [6 empty] | 0.164 | 0.098 | 30 | [6 empty] | 0.164 | 0.098 | 30 | 0.1 | 0.3
2008-11-12 |  |  |  | 0.111 | 0.085 | 15 | [6 empty] | 0.111 | 0.085 | 15 |  |  |  | 0.1 | 0.3
2008-11-13 | 0.117 | 0.088 | 17 | [6 empty] | 0.117 | 0.088 | 17 | [6 empty] | 0.1 | 0.3
2008-11-14 | [6 empty] | 0.131 | 0.113 | 28 | [6 empty] | 0.131 | 0.113 | 28 | 0.1 | 0.3
2008-11-15 |  |  |  | 0.156 | 0.097 | 26 | [6 empty] | 0.156 | 0.097 | 26 |  |  |  | 0.1 | 0.3
2008-11-16 | 0.136 | 0.098 | 25 | [6 empty] | 0.136 | 0.098 | 25 | [6 empty] | 0.1 | 0.3
2008-11-17 |  |  |  | 0.157 | 0.096 | 21 | 0.202 | 0.127 | 30 |  |  |  | 0.157 | 0.096 | 21 | 0.202 | 0.127 | 30 | 0.1 | 0.3
2008-11-18 | [18 empty] | 0.1 | 0.3
2008-11-19 | 0.129 | 0.099 | 18 | 0.193 | 0.095 | 20 | 3 | 1.461 | 32 | 0.129 | 0.099 | 18 | 0.193 | 0.095 | 20 | 3 | 1.461 | 32 | 0.1 | 0.3
2008-11-20 | [18 empty] | 0.1 | 0.3
2008-11-21 | 0.151 | 0.099 | 26 |  |  |  | 0.222 | 0.186 | 30 | 0.151 | 0.099 | 26 |  |  |  | 0.222 | 0.186 | 30 | 0.1 | 0.3
2008-11-22 |  |  |  | 0.183 | 0.099 | 19 | [6 empty] | 0.183 | 0.099 | 19 |  |  |  | 0.1 | 0.3
2008-11-23 | 0.142 | 0.121 | 38 | [6 empty] | 0.142 | 0.121 | 38 | [6 empty] | 0.1 | 0.3
2008-11-24 | [6 empty] | 0.256 | 0.214 | 34 | [6 empty] | 0.256 | 0.214 | 34 | 0.1 | 0.3
2008-11-25 | 0.369 | 0.361 | 30 | 0.269 | 0.197 | 30 |  |  |  | 0.369 | 0.361 | 30 | 0.269 | 0.197 | 30 |  |  |  | 0.1 | 0.3
2008-11-26 | [18 empty] | 0.1 | 0.3
2008-11-27 | [18 empty] | 0.1 | 0.3
2008-11-28 |  |  |  | 0.122 | 0.094 | 13 | 0.153 | 0.09 | 20 |  |  |  | 0.122 | 0.094 | 13 | 0.153 | 0.09 | 20 | 0.1 | 0.3
2008-11-29 | 0.12 | 0.092 | 17 | [6 empty] | 0.12 | 0.092 | 17 | [6 empty] | 0.1 | 0.3
2008-11-30 | [18 empty] | 0.1 | 0.3
2008-12-01 |  |  |  | 0.118 | 0.091 | 12 | [6 empty] | 0.118 | 0.091 | 12 |  |  |  | 0.1 | 0.3
2008-12-02 | 0.22 | 0.188 | 30 |  |  |  | 0.229 | 0.161 | 30 | 0.22 | 0.188 | 30 |  |  |  | 0.229 | 0.161 | 30 | 0.1 | 0.3
2008-12-03 | [18 empty] | 0.1 | 0.3
2008-12-04 |  |  |  | 0.289 | 0.289 | 32 | [6 empty] | 0.289 | 0.289 | 32 |  |  |  | 0.1 | 0.3
2008-12-05 | [18 empty] | 0.1 | 0.3
2008-12-06 | [6 empty] | 0.15 | 0.15 | 30 | [6 empty] | 0.15 | 0.15 | 30 | 0.1 | 0.3
2008-12-07 | 0.099 | 0.092 | 12 | 0.085 | 0.072 | 12 |  |  |  | 0.099 | 0.092 | 12 | 0.085 | 0.072 | 12 |  |  |  | 0.1 | 0.3
2008-12-08 | [18 empty] | 0.1 | 0.3
2008-12-09 | [6 empty] | 0.13 | 0.103 | 25 | [6 empty] | 0.13 | 0.103 | 25 | 0.1 | 0.3
2008-12-10 | 0.114 | 0.106 | 13 | [6 empty] | 0.114 | 0.106 | 13 | [6 empty] | 0.1 | 0.3
2008-12-11 | [18 empty] | 0.1 | 0.3
2008-12-12 | [6 empty] | 0.145 | 0.12 | 30 | [6 empty] | 0.145 | 0.12 | 30 | 0.1 | 0.3
2008-12-13 | 0.086 | 0.079 | 12 | [6 empty] | 0.086 | 0.079 | 12 | [6 empty] | 0.1 | 0.3
2008-12-14 |  |  |  | 0.079 | 0.063 | 11 | 0.142 | 0.11 | 30 |  |  |  | 0.079 | 0.063 | 11 | 0.142 | 0.11 | 30 | 0.1 | 0.3
2008-12-15 | [18 empty] | 0.1 | 0.3
2008-12-16 |  |  |  | 0.087 | 0.069 | 17 | 0.116 | 0.105 | 25 |  |  |  | 0.087 | 0.069 | 17 | 0.116 | 0.105 | 25 | 0.1 | 0.3
2008-12-17 |  |  |  | 0.088 | 0.075 | 12 | [6 empty] | 0.088 | 0.075 | 12 |  |  |  | 0.1 | 0.3
2008-12-18 | [18 empty] | 0.1 | 0.3
2008-12-19 | [6 empty] | 0.332 | 0.105 | 21 | [6 empty] | 0.332 | 0.105 | 21 | 0.1 | 0.3
2008-12-20 | 0.12 | 0.1 | 21 | 0.107 | 0.096 | 12 |  |  |  | 0.12 | 0.1 | 21 | 0.107 | 0.096 | 12 |  |  |  | 0.1 | 0.3
2008-12-21 | [18 empty] | 0.1 | 0.3
2008-12-22 | [18 empty] | 0.1 | 0.3
2008-12-23 |  |  |  | 0.096 | 0.081 | 12 | [6 empty] | 0.096 | 0.081 | 12 |  |  |  | 0.1 | 0.3
2008-12-24 | [6 empty] | 0.169 | 0.064 | 12 | [6 empty] | 0.169 | 0.064 | 12 | 0.1 | 0.3
2008-12-25 | [18 empty] | 0.1 | 0.3
2008-12-26 | [18 empty] | 0.1 | 0.3
2008-12-27 | [18 empty] | 0.1 | 0.3
2008-12-28 | [18 empty] | 0.1 | 0.3
2008-12-29 | [18 empty] | 0.1 | 0.3
2008-12-30 | [18 empty] | 0.1 | 0.3
2008-12-31 | [18 empty] | 0.1 | 0.3
Note on C15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on D15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on E15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on F15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on G15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on H15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on I15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on J15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on K15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on L15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on M15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on N15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on O15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on P15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on Q15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Note on R15: Plants with filter-to-waste (FTW) capability: Input maximum turbidity during FTW period. Plants without FTW capability: Input maximum turbidity during 15 minutes following return to service.
Note on S15: Plants with Filter-to-waste (FTW) capability: Input turbidity before filter is returned to service (RTS). Plants without FTW capability: Input turbidity 15 minutes after filter is returned to service.
Note on T15: Plants with filter-to-waste (FTW) capability: Input FTW time in minutes.
Clear Database