## Test Results
Lead in Water Test Results Summary: |  | Paige Turner High School - Main Building
Notes:
• The lead in water Action Level is 10 parts per billion (ppb).
Any fixture testing at or above the action level of 10 ppb is immediately removed from service and cannot be returned to service until it has been remediated and passed follow-up testing.
• A "ND" or "non-detect" test result indicates the sample measured below the minimum detection limit of 1 ppb.
Legend:
• Test results greater than or equal to the Action Level of 10 ppb are highlighted in red and precede an "Action Req." (Action Required) value in the "Initial Level" or "Final Level" column.
• Test results from 8 ppb to 9.99 ppb (near the Action Level) are highlighted in orange and precede a "High" value in the "Initial Level" or "Final Level" column.
• Test results from 5 ppb to 7.99 ppb are highlighted in yellow and precede a "Moderate" value in the "Initial Level" or "Final Level" column.
• Test results less than 5 ppb are not highlighted and precede a "Low" value in the "Initial Level" or "Final Level" column.
Fixture Location Description | Fixture ID # | Initial Test Date | Initial Test Result (ppb) | Initial Level | Final Retest Date | Final Test Result (ppb) | Final Level
Main hall - Drinking Fountain upper | 12340101-001DW | 2022-04-11 | 2.3 | Low
Main hall - Drinking Fountain lower | 12340101-002DW | 2022-04-11 | 2.5 | Low
Main wing - Boys Restroom sink left | 12340101-003BF | 2022-04-11 | ND | Non-Detect
Main wing - Boys Restroom sink right | 12340101-004BF | 2022-04-11 | 1.1 | Low
Main wing - Girls Restroom sink left | 12340101-005BF | 2022-04-11 | 5.1 | Moderate
Main wing - Girls Restroom sink right | 12340101-006BF | 2022-04-11 | 8.2 | High
Art room - North sink | 12340101-007CF | 2022-04-11 | 23.6 | Action Req. | 2022-05-13 | ND | Non-Detect
Art room - South sink | 12340101-008CF | 2022-04-11 | 13.7 | Action Req. | 2022-05-13 | 1.4 | Low