## General Guidance
General Guidance on Using the Facility Assessment Template
1 | Before completing the template it is best to do an informal interview with the individual in charge of the facilities. This is especially helpful when completing the checklists e.g., ADA, Harmful Substances, etc.
2 | Please ensure that you are interviewing the correct person to complete the checklists. For example, you may need to talk to the Internet Service Provider to complete the IT checklist.
3 | It is recommended that you complete the assessment on-site. Enter percentages and levels of action on-site after the walkthrough and before leaving the facility.
4 | For the template to accurately calculate information please complete the Base Information tab. Cells highlighted in yellow are required as the rest of the template’s formulas will not calculate correctly without that information.
5 | For the template to function properly do not change information on the READ ONLY tabs (worksheets e.g., "Building Type Budget-READ ONLY").
6 | Make sure you hover over the upper right-hand corner of cells to view comments.
7 | They determine the level of action. Pay attention to whether a comment says “and” or “or.”
8 | Type a capital letter X or select X from the drop-down menu to indicate the LEVEL OF ACTION for a system that is present.
9 | To indicate a system is not present, enter the numeric value zero “0” in the % of Building or Count column.
10 | When entering data in the % of System or Finish Affected column (Column S), the data must be entered as a percentage of the system. For example, if resilient tile covers 50% of the building and 35% of it needs to be replaced, enter 35 in the % of System or Finish Affected column. This is true even if the system uses a different unit of measure rather than the percentage of gross square feet. For example, if there are 40 wood doors and 10 need to be replaced, enter 25 in % of System or Finish Affected column (Column S).
11 | When you are using your expertise to override the built-in cost model document, note that decision in the Notes column. Notes must be added so that the state and districts know why you are overriding the template. For example, a system has a key component that needs to be replaced but that replacement is not accurately described in the LEVEL OF ACTION comments.
12 | If you have a system not found in the template then add it at the bottom of the Physical Condition Assessment tab under OTHER.
13 | If you know that costs have changed, override the cost on the Physical Condition Assessment tab ONLY and note it.
14 | Please note that while gross square footage is used in the Automated Budget Estimate formula for most building systems, some systems will use a different unit of measure. Be sure to check the notes in Columns C, D, and/or E that indicate whether to enter count, total linear feet, surface area, etc. For some systems in the % of Building or Count column (Column E), you will enter the quantity or number of units as described rather than the % of the building's gross square footage. This applies to B2030 Exterior Doors, B3020 Roof Openings - Access Hatch, C1020 Interior Doors, C20 Stairs, D10 Conveying, E1020 Institutional Equipment, G20 Site Improvements, G30 Site Mechanical Utilities, and G4010 Electrical Distribution - Generator.
15 | Please create a different assessment Excel workbook for each building.
16 | The default for portables is to list them in the Renovations, Additions, & Prtbls tab. If a district requests a full assessment of their portable classrooms, please create a separate assessment Excel workbook for each building.
17 | If an ADA deficiency is listed in the Physical Condition Assessment tab, then include that in the final costs. However, please do not add costs to the final amounts simply to bring the building into ADA compliance.

## Base Information
Item | Data | Notes / Explanation
District Name: |  | Pull-down menu of the 197 Districts and 19 ESDs (alphabetical order)
Site Name: |  | Typically the name that is used for the facility / campus
Building Name: |  | If only one building on site, refer to "main"
Building ID: |  | Use the School Facilities Building Collection Building ID Number (BIN) Lookup Tool for the eight (8) digit number assigned to the building. To use the tool, first download a copy of it by selecting File -> Save As -> Download a Copy. At the top of the Lookup Tool, enter the District ID which you can find on the Entity ID tab.
Building Type: |  | Pull-down menu - feeds FCI calculation
Physical Address of Building: |  | Informational only - does not link
Original Year of Building Completion: |  | When was the original building completed and ready for use
Primary Structure Type: |  | Pull-down menu of primary building construction / structure types
Secondary Structure Type: |  | Pull-down menu of secondary building construction / structure types
County: |  | Pull-down menu of the 36 counties - sets location factor for budgets
Gross Square Footage: |  | Calculated from exterior face of walls (excluding eaves, outbuilding, porches, canopies, and similar)
Site Acreage: |  | District records
Assessor Company:
Assessor Name: |  | For follow up questions
Contact (Phone):
Contact (E-Mail):
Date of Assessment: | 0/0/0000 | Enter the actual date of the assessment - use m/d/yyyy format
Version: 11/15/2023

## Structure Types (hidden)
W1 – Wood, Light Frame, Single Dwelling
W1A – Wood, Light Frame, Multi-Unit
W2 – Wood, Commercial and Industrial
C1 – Concrete Moment Resisting Frame
C2 – Concrete Shear Walls
C3 – Concrete Frame with Unreinforced Masonry Infill Walls
RM1 – Reinforced Masonry Bearing Walls With Wood or Metal Deck Diaphragm
RM2 – Reinforced Masonry Bearing Walls With Precast Concrete Diaphragm
URM – Unreinforced Masonry Bearing Walls
S1 – Steel Moment Frame
S2 – Steel Braced Frame
S3 – Steel Light Frame
S4 – Steel Frame with Case-In-Place Concrete Shear Walls
S5 – Steel Frame with Unreinforced Masonry Infill Walls
MH – Mobile Home
OTH – Other
PC1 – Tilt-Up Buildings
PC2 – Precast concrete frame buildings

## Renovations, Additions & Prtbls
A. RENOVATIONS
Renovation Number | Date | Primary Structure Type | Secondary Structure Type (if applicable) | Square Footage | Usage
none
B. ADDITIONS
Addition Number | Date | Primary Structure Type | Secondary Structure Type (if applicable) | Square Footage | Usage
none
C. PORTABLE CLASSROOMS
Portable Number | Date Placed on Site | Age of Portable | Primary Structure Type | Square Footage | Notes
none

## Physical Condition Assessment
District Name: |  | (autofill) |  |  | REMINDER: FILL OUT ALL INFORMATION ON 'BASE INFORMATION SHEET' BEFORE ENTERING DATA ON THIS SHEET
Site Name: |  | (autofill) |  |  |  | An unused cell or system that should not receive direct user input
Building Name: |  | (autofill) |  |  |  | An automatically populated cell from user input elsewhere in the file - do not overwrite
Building ID: |  | (autofill) |  |  |  | Enter Voter Approved Bond Date and adjust the number of months for design and construction as needed
Date of Estimate: |  | (autofill)
Renovation Schedule |  | Voter Approved Bond Date: | 2024-11-05
|  | Design Finish Date: | 2025-11-05 | Default is | 12 | months after bond
|  | Construction Start Date: | 2025-11-05 | Default is | at design finish
|  | Construction End Date: | 2027-11-05 | Default is | 24 | month construction period
Replacement Schedule |  | Voter Approved Bond Date: | 2024-11-05 | Default is | 12 | months after estimate
|  | Design Finish Date: | 2025-11-05 | Default is | 12 | months after bond
|  | Construction Start Date: | 2025-11-05 | Default is | at design finish
|  | Construction End Date: | 2027-11-05 | Default is | 24 | month construction period
LEVEL OF ACTION (Select 'X' in drop down if applicable)
Level 1 | Level 2 | Level 3 | Type (as applicable) | % of Building or Count |  |  | None | Minor |  | Moderate | Major | Replace as Part of Renovation |  | Replace as Singular Scope | % of System or Finish Affected | Automated Budget Estimate | Add to Escalate to 11/5/2026 (Renovation Construction Midpoint) | Escalated to 11/5/2026 (Renovation Construction Midpoint) | Escalated to 11/5/2027 (Renovation Construction Midpoint) | Escalated to 11/5/2028 (Renovationt Construction Midpoint) | Notes
A SUBSTRUCTURE
A10 Foundations
|  | A1010 Standard Foundations |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | A1020 Special Foundations |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | A1030 Slab on Grade |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
A20 Basement Construction
|  | A2010 Basement Excavation | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
|  | A2020 Basement Walls |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
B SHELL
B10 Superstructure
|  | B1010 Floor Construction | Wood |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Steel |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Concrete |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | B1020 Roof Construction | Wood |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Steel |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Concrete |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
B20 Exterior Enclosure
|  | B2010 Exterior Walls | Concrete Formed / Tilt |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Masonry |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Framed w/ Wood Siding |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Framed w/Metal Panel |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Framed w/Stucco |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Framed w/Masonry Veneer |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | B2020 Exterior Windows | Wood |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Aluminum/Steel |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Clad |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Curtain Wall |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | B2030 Exterior Doors | Wood |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Hollow Metal |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Storefront |  |  |  | None | Minor |  | Moderate | Major | Replace |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| B30 Roofing | [12 empty] | Replace
|  | B3010 Roof Coverings | Asphalt Shingle |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Built-Up |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Single Ply |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Metal |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Concrete Tile |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | B3020 Roof Openings | Skylights |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | By Building GSF
|  |  | Access Hatch |  |  |  | None | Minor | 1 | Moderate | Major | Replace |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Per hatch
C INTERIORS
C10 Interior Construction
|  | C1010 Partitions | Framed |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Masonry |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | C1020 Interior Doors | Wood |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Hollow Metal |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | C1030 Fittings | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
C20 Stairs
|  | C2010 Stair Construction | Wood |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/Flight
|  |  | Metal |  |  |  | None | Minor |  | Moderate | Major | Replace |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/Flight
|  |  | Concrete |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/Flight
|  | C2020 Stair Finishes | Concrete Fill |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/Flight
|  |  | Resilient |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/Flight
C30 Interior Finishes
|  | C3010 Wall Finishes | Paint on Masonry |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Wallboard |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Wainscot |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Ceramic Tile |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | C3020 Floor Finishes | Carpet / Soft Surface |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Resilient Tile |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Resilient Sheet |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Polished Concrete |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Ceramic Tile |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Liquid Applied |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Wood Sports Floor |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | C3030 Ceiling Finishes | Wallboard |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Lay-In Ceiling Tile |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Glued-Up Ceiling Tile |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Painted Structure |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
D SERVICES
D10 Conveying
|  | D1010 Elevators & Lifts |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D1020 Escalators & Moving Walks |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D1090 Other Conveying Systems |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
D20 Plumbing
|  | D2010 Plumbing Fixtures |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | All (N) fixtures must meet ADA requirements by code.
|  | D2020 Domestic Water Distribution |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D2030 Sanitary Waste |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D2040 Rain Water Drainage |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D2090 Other Plumbing Systems | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
D30 HVAC
|  | D3010 Energy Supply |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D3020 Heat Generating Systems | Boiler |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Air Handler |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Furnace |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Heat Exchanger |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D3030 Cooling Generating Systems | Component of air handler |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Stand alone chiller |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D3040 Distribution Systems | Ductwork |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Hot water return & supply |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D3050 Terminal & Package Units | Above ceiling VAV unit |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | In-room ventilator unit |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | In-room radiant unit |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D3060 Controls & Instrumentation |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D3070 Systems Testing & Balancing |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D3090 Other HVAC Systems & Equipment | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
D40 Fire Protection
|  | D4010 Sprinklers |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D4020 Standpipes |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D4030 Fire Protection Specialties |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D4090 Other Fire Protection Systems | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
D50 Electrical
|  | D5010 Electrical Service & Distribution |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D5020 Lighting and Branch Wiring |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D5030 Communications & Security | Voice / Data System |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Clock / Intercom System |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Closed Circuit Surveillance |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Access Control System |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Intrusion Alarm System |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Fire Alarm / Detection |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Lighting Control System |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | D5090 Other Electrical Systems | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
E EQUIPMENT & FURNISHINGS
E10 Equipment
|  | E1010 Commercial Equipment | Food Service |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Vocational |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | E1020 Institutional Equipment | Science |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Art |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Stage Performance |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/SF of Stage Performance Area
|  |  | Restroom Accessories/Stalls |  |  |  | None | Minor |  | Moderate | Major | Replace |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | E1030 Vehicular Equipment | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
|  | E1090 Other Equipment | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
E20 Furnishings
|  | E2010 Fixed Furnishings |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | E2020 Movable Furnishings |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
F SPECIAL CONSTRUCTION & DEMOLITION - NOT USED
G BUILDING SITE WORK
| G10 Site Preparation |  | NOT USED
G20 Site Improvements
|  | G2010 Roadways |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/SF of surface area
|  | G2020 Parking Lots |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/SF of surface area
|  | G2030 Pedestrian Paving |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/SF of surface area
|  | G2040 Site Development |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/LF of fencing
|  | G2050 Landscaping |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Cost/SF of irrigated area
G30 Site Mechanical Utilities
|  | G3010 Water Supply | Domestic |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Enter LF of pipe in cell E154
|  |  | Fire |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Enter LF of pipe in cell E155
|  | G3020 Sanitary Sewer |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Enter LF of sewer lines in cell E156
|  | G3030 Storm Sewer |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Enter SF of area to be drained
|  | G3040 Heating Distribution |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Enter LF of heating ducts in cell E158
|  | G3050 Cooling Distribution |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Enter LF of duct work in cell E159
|  | G3060 Fuel Distribution |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Enter LF of natural gas lines in cell E160
|  | G3090 Other Site Mechanical Utilities | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace
G40 Site Electrical Utilities
|  | G4010 Electrical Distribution | Service |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Generator |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | G4020 Site Lighting |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | G4030 Site Communications & Security |  |  |  |  | None | Minor |  | Moderate | Major | Replace |  | Replace |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | G4090 Other Site Electrical Utilities | NOT USED |  |  |  | None | Minor |  | Moderate | Major | Replace | x | Replace
| G90 Other Site Construction |  | NOT USED
OTHER
| Description of System | [8 empty] | Unit of Measure | Quantity | Unit Budget |  | Unit Budget |  | Total Budget | Add to Extend | Extended | Extended | Extended | Notes
[16 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[16 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[16 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[16 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[16 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[16 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[16 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | Renovation Costs | Physical Condition Budget Sub-Total |  |  |  |  | #VALUE!
[11 empty] | Budgeted Development Costs |  |  |  |  | #VALUE!
[11 empty] | Physical Condition Budget TOTAL |  |  |  |  | #VALUE!
[11 empty] | Cost with Escalation to (construction mid point): |  |  |  | 2026-11-05 | #VALUE! | *Escalation to projected construction mid point, per schedule entered
[11 empty] | Cost with Escalation to: |  |  |  | 2027-11-05 | #VALUE! | *Escalation to projected construction mid point + 1 year
[11 empty] | Cost with Escalation to: |  |  |  | 2028-11-05 | #VALUE! | *Escalation to projected construction mid point + 2 years
[10 empty] | Replacement Costs | Replacement Budget |  |  |  |  | 0
[11 empty] | Facility Condition Index (FCI) |  |  |  |  | n/a
Note on C21: Standard spread and strip/perimeter footings. Based on building's gross square footage.
Note on I21: Minor cracking observed - fill and seal the cracks to prevent water intrusion.
Note on M21: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation.
Note on C22: Pilings or other extended foundation systems that overcome non-standard soil conditions. Based on building's gross square footage.
Note on I22: Minor cracking observed - fill and seal the cracks to prevent water intrusion.
Note on M22: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation.
Note on C23: Standard ground-set concrete slab. If slab is elevated, i.e. has a crawl space or basement, apply conditions to B1010 instead. Based on building's gross square footage.
Note on K23: Separation cracks occurring requiring route and fill and patch.
Note on M23: Differential settlement occurring - requires removal of section of slab, adjustment to sub-grade, and new infill.
Note on C26: Assumed as concrete walls with water-proofing on the exterior. Includes only the structural portion and not the wall finishes. Based on building's gross square footage.
Note on I26: Inadequate below grade venting is observed - cut in and add venting.
Note on K26: Wall is cracked and spalling requiring route and fill and patch and re-finish.
Note on M26: Wall is cracked with evidence of water intrusion. Repairs to be implemented and water barrier to be applied to be applied.
Note on C29: A suspended floor including the structural members and floor construction, but not including the actual finish.
Note on K29: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on O29: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on Q29: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on K30: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on O30: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on Q30: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on K31: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on O31: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on Q31: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on C32: The roof structure referring to the supporting structure and the deck but excluding the roofing itself.
Note on M32: Evidence of a spongy decking from water intrusion - replacing the deck but not the trusses.
Note on O32: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on Q32: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on M33: Evidence of a flexing decking from water intrusion/rust - replacing the deck but not the trusses.
Note on O33: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on Q33: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on M34: Evidence of a spongy/spalling deck from water intrusion - replacing the deck but not the beams.
Note on O34: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on Q34: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on K36: Surface is intact but finish is deteriorated - paint.
Note on M36: Cracks visible - route and patch prior to painting.
Note on K37: Surface is intact but finish is deteriorated - paint.
Note on M37: Some blocks are damaged, needing patch and repair prior to sealing or painting.
Note on O37: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on Q37: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on K38: Surface is intact but finish is deteriorated - paint.
Note on M38: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on O38: The panels are lifting or separating or otherwise losing their integrity - remove and replace.
Note on Q38: The panels are lifting or separating or otherwise losing their integrity - remove and replace
Note on K39: Surface is intact but finish is deteriorated - paint.
Note on M39: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on O39: The panels are lifting or separating or otherwise losing their integrity - remove and replace.
Note on Q39: System in failure with evidence of water intrusion - remove and replace
Note on K40: Surface is in tact but finish is deteriorated - paint.
Note on M40: Cracks visible - route and patch prior to painting.
Note on O40: System in failure with evidence of water intrusion - remove and replace.
Note on Q40: Masonry visibly damaged and requiring removal and replacement
Note on K41: Minor repairs needed to mortar, prep, and re-sealing.
Note on M41: Mortar missing in a majority of areas requiring complete re-pointing and sealing.
Note on O41: Masonry visibly damaged and requiring removal and replacement.
Note on Q41: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on K42: The glazing is double pane but is broken or fogged and requires replacement.
Note on M42: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on O42: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on Q42: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D43: This assumes both individual aluminum windows and storefront systems.
Note on K43: The glazing is double pane but is broken or fogged and requires replacement.
Note on M43: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on O43: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on Q43: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D44: This assumes a metal windows system clad with wood or vinyl.
Note on K44: The glazing is double pane but is broken or fogged and requires replacement.
Note on M44: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on O44: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on Q44: Settlement or displacement is evident
Note on K45: Minor leaks at wall seams - re-caulk and re-seal.
Note on M45: Window panels fogged and require replacement.
Note on O45: Settlement or displacement is evident.
Note on Q45: Door frame, door, and hardware are damaged and require replacement
Note on D46: Apply to door count.
Note on K46: Door hardware is damaged or non-functional and requires replacement.
Note on M46: Door panel and hardware are damaged and require replacement.
Note on O46: Door frame, door, and hardware are damaged and require replacement.
Note on Q46: Door frame, door, and hardware are damaged and require replacement
Note on D47: Apply to door count.
Note on K47: Door hardware is damaged or non-functional and requires replacement.
Note on M47: Door panel and hardware are damaged and require replacement.
Note on O47: Door frame, door, and hardware are damaged and require replacement.
Note on Q47: Door frame, door, and hardware are damaged and require replacement
Note on D48: Apply to door count.
Note on K48: Door hardware is damaged or non-functional and requires replacement.
Note on M48: Door panel and hardware are damaged and require replacement.
Note on O48: Door frame, door, and hardware are damaged and require replacement.
Note on Q49: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on C50: Assumes the insulation, roof covering, and associated flashings, gutters, and downspouts.
Note on I50: Small number of shingles lifting and/or separation in a portion of flashing.
Note on K50: Leaks in a specific area or zone related to poor detailing and / or flashing.
Note on M50: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING.
Note on O50: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND REPLACE roof system.
Note on Q50: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on I51: Minor blistering requiring isolated patches.
Note on K51: Leaks in a specific area or zone related to poor detailing and / or flashing or unchecked blisters.
Note on M51: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING.
Note on O51: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND REPLACE roof system.
Note on Q51: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on I52: Minor blistering requiring isolated patches.
Note on K52: Leaks in a specific area or zone related to poor detailing and / or flashing or seam separation.
Note on M52: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Prep and re-coat roof system OVER TOP OF EXISTING.
Note on O52: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND REPLACE roof system.
Note on Q52: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Note on K53: Leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing and sealant.
Note on O53: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing.
Note on Q53: Tiles are cracked, loose, or damaged and require removal and replacement
Note on K54: Leaks occurring at isolated areas requiring grout removal and re-grout at isolated tile locations.
Note on O54: Tiles are cracked, loose, or damaged and require removal and replacement.
Note on Q54: The panes or framing are damaged beyond repair and requires replacement
Note on D55: Based on building's gross square footage.
Note on K55: Minor leaking is occurring, requiring re-caulk and re-seal.
Note on O55: The panes or framing are damaged beyond repair and requires replacement.
Note on Q55: The door is non-functional or damaged beyond repair and requires replacement
Note on D56: Apply to access hatch count.
Note on O56: The door is non-functional or damaged beyond repair and requires replacement.
Note on O59: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on Q59: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on M60: There are some blocks that are damaged and requires a strategic removal and replacement.
Note on O60: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on Q60: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on D61: Apply to door count.
Note on K61: Door hardware is damaged or non-functional and requires replacement.
Note on M61: Door panel and hardware are damaged and require replacement.
Note on O61: Door frame, door, and hardware are damaged and require replacement.
Note on Q61: Door frame, door, and hardware are damaged and require replacement
Note on D62: Apply to door count.
Note on K62: Door hardware is damaged or non-functional and requires replacement.
Note on M62: Door panel and hardware are damaged and require replacement.
Note on O62: Door frame, door, and hardware are damaged and require replacement.
Note on Q62: Door frame, door, and hardware are damaged and require replacement
Note on D65: Apply to stair flights.
Note on M65: Rails not compliant with code and require removal and replacement.
Note on O65: Structural integrity of stair unit is compromised and requires its removal and replacement.
Note on Q65: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on D66: Apply to stair flights.
Note on I66: Rust visible - prep and re-finish.
Note on M66: Rails not compliant with code and require removal and replacement.
Note on O66: Structural integrity of stair unit is compromised and requires its removal and replacement.
Note on Q66: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on D67: Apply to stair flights.
Note on M67: An isolated structural crack or separation requiring re-enforcement in place.
Note on O67: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit.
Note on Q67: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit
Note on D68: Apply to stair flights.
Note on I68: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal.
Note on O68: Severe cracking requiring removal and replacement of tread in fills.
Note on Q68: Severe cracking requiring removal and replacement of tread in fills
Note on D69: Apply to stair flights.
Note on O69: Finish is lifting or separating and creating trip hazards - remove and replace.
Note on Q69: finish is lifting or separating and creating trip hazards - remove and replace
Note on I71: Surface is intact but finish is deteriorated - paint.
Note on O71: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on Q71: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on I72: Surface is intact but finish is deteriorated - paint.
Note on K72: Surface is damaged - patching of the surface is required prior to painting.
Note on O72: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on Q72: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on I73: Surface is intact but finish is deteriorated - paint.
Note on O73: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on Q73: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on I74: Grout is damaged or deteriorated.
Note on O74: Tiles are cracked or in disrepair.
Note on Q74: Tiles are cracked or in disrepair
Note on O75: Worn or severely stained or starting to pull up/bubble.
Note on Q75: worn or severely stained or starting to pull up / bubble
Note on I76: Sporadic number of tiles are lifting or cracked/broken and require replacement.
Note on M76: The majority of tiles are lifting, cracking/broken and require replacement - the tiles or glue are NOT asbestos.
Note on O76: The majority of tiles are lifting, cracking/broken and require replacement - the tiles or glue are asbestos.
Note on Q76: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are asbestos
Note on O77: Severely worn or seams separating - replace.
Note on Q77: Severely worn or seams separating - replace
Note on I78: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal.
Note on O78: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above.
Note on Q78: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above
Note on I79: Grout is damaged or deteriorated.
Note on O79: Tiles are cracked or in disrepair.
Note on Q79: Tiles are cracked or in disrepair
Note on O80: Systemic blistering or severely worn traffic areas - strip and replace.
Note on Q80: Systemic blistering or severely worn traffic areas - strip and replace
Note on K81: Surface is damaged - requires sanding, repair, and re-coat/re-stripe.
Note on O81: Wood planks are deteriorated, separating, and multiple dead spots - replace floor.
Note on Q81: Wood planks are deteriorated, separating, and multiple dead spots - replace floor
Note on I82: Surface is in tact but finish is deteriorated - paint.
Note on K82: Surface is damaged - patching of the surface is required prior to painting.
Note on O82: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on Q82: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on I83: Stained or damaged ceiling tiles.
Note on K83: Diagonal bracing missing from grid.
Note on O83: Grid is sagging with tiles compromised - requires replacement of system.
Note on Q83: Grid is sagging with tiles compromised - requires replacement of system
Note on I84: Stained or damaged ceiling tiles.
Note on O84: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on Q84: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on O85: Surface is in tact but finish is deteriorated - paint.
Note on Q85: Surface is in tact but finish is deteriorated - paint
Note on C88: Assume standard cab-style elevator. Apply per stop.
Note on E88: Insert number of elevators multiplied by number of stories, e.g., if there are 2 escalators each going 3 stories, enter 6.
Note on I88: The elevator doors are damaged and require replacement.
Note on K88: Electrical components are not working.
Note on M88: Replacement of the hoist cables, guide rails, or other similar mechanical components is required.
Note on O88: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on Q88: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C89: Apply per flight.
Note on E89: Insert number of escalators multiplied by number of stories, e.g., if there are 2 escalators each going 3 stories, enter 6.
Note on K89: Electrical components are not working.
Note on O89: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on Q89: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C90: Assume open vertical or inclined lift. Apply per unit.
Note on E90: Insert number of lifts.
Note on K90: Electrical components are not working.
Note on O90: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on Q90: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C92: All fixtures (toilets, urinals, sinks, showers, etc.) to be lumped together here.
Note on K92: Flush valves or faucets are non-functional and require replacement.
Note on O92: The fixture itself is broken or is not compliant with water efficiency standards.
Note on Q92: The fixture itself is broken or is not compliant with water efficiency standards
Note on I93: The vale stems, pressure gauges, and gate valves no longer function.
Note on K93: The insulation on the piping is in disrepair, loose, or missing.
Note on O93: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on Q93: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on I94: In some areas, there are back-ups requiring the replacement of the broken floor or wall, clean outs, routing and cleaning the problem areas, and snaking floor drains.
Note on O94: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement.
Note on Q94: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Note on C95: This is for the presence of interior rain drains. Excludes external downspouts. Based on gross square footage.
Note on K95: The rain drain or overflow is damaged and needs replacement.
Note on O95: The integrity of the piping is compromised and is leaking inside the walls.
Note on Q95: The integrity of the piping is compromised and is leaking inside the walls
Note on C98: This assumes gas piping.
Note on I98: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on O98: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on Q98: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on I99: The burner is inefficient and requires refurbishment.
Note on K99: One major component needs to be replaced.
Note on M99: More than one major component needs to be replaced.
Note on O99: The system is in failure.
Note on Q99: The system is in failure
Note on M100: Some of the distribution fans and coils are dysfunctional.
Note on O100: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair.
Note on Q100: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on K101: A small number of minor parts need to be repaired or replaced.
Note on M101: The burner, combustion chamber, or fan are faulty and require replacement.
Note on O101: The entire furnace requires replacement.
Note on Q101: The entire furnace requires replacement
Note on K102: A small number of minor parts need to be repaired or replaced.
Note on M102: System operating at low efficiency; shell exhibits corrosion. Retube heat exchanger.
Note on O102: System operates at low efficiency with corrosion and leaks apparent. Replace system.
Note on Q102: System operates at low efficiency with corrosion and leaks apparent. Replace system
Note on M103: Some of the distribution fans and coils are dysfunctional.
Note on O103: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair.
Note on Q103: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on O104: The chiller is beyond economic repair.
Note on Q104: The chiller is beyond economic repair
Note on K105: Dampers in the system are inoperative.
Note on M105: The insulation is damaged or missing.
Note on O105: The ductwork is damaged or inadequately designed and requires replacement.
Note on Q105: The ductwork is damaged or inadequately designed and requires replacement
Note on I106: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on K106: The insulation on the piping is in disrepair, loose, or missing.
Note on O106: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on Q106: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on O107: Entire unit is failing to function.
Note on Q107: Entire unit is failing to function
Note on K108: Internal compressor is bad and requires replacement.
Note on O108: Entire unit is failing to function.
Note on Q108: Entire unit is failing to function
Note on I109: In-room valve is failing and requires replacement.
Note on O109: Entire unit is failing to function.
Note on Q109: Entire unit is failing to function
Note on M110: Some of the sensors or valve actuators are dysfunctional. Replace these sensors or actuators.
Note on O110: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older/obsolete pneumatic system - replace.
Note on Q110: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system - replace
Note on O111: One or more zones require re-balancing.
Note on Q111: One or more zones require re-balancing
Note on K114: Sprinkler heads are inoperable or non-compliant and need to be replaced.
Note on O114: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads.
Note on Q114: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads
Note on K115: The Siamese twin connection, tamper flow switches, or flow control valves are inoperable and need to be replaced.
Note on O115: The fire pump is beyond repair and needs to be replaced.
Note on Q115: The fire pump is beyond repair and needs to be replaced
Note on C116: Assume chemical extinguishing system.
Note on K116: The back-up tank has been discharged or lacks pressure and needs to be replaced.
Note on O116: The system is non-functional or not compliant with the current needs and needs to be replaced.
Note on Q116: The system is non-functional or not compliant with the current needs and needs to be replaced
Note on K119: Wiring has systemic problems or does not meet code and needs to be replaced.
Note on M119: Branch panels are obsolete with replacement breakers difficult to acquire and requires replacement.
Note on O119: Main switchgear is obsolete or undersized and requires replacement, including service into building.
Note on Q119: Main switchgear is obsolete or undersized and requires replacement, including service into building
Note on M120: The lighting fixtures are obsolete or non-functional and require replacement.
Note on O120: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring.
Note on Q120: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring
Note on K121: There are individual devices that are not functional.
Note on M121: The master control panel is obsolete or not functional.
Note on O121: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on Q121: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on K122: There are individual devices that are not functional.
Note on M122: The master control panel is obsolete or not functional.
Note on O122: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on Q122: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on K123: There are individual devices that are not functional.
Note on M123: The master control panel is obsolete or not functional.
Note on O123: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on Q123: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on K124: There are individual devices that are not functional.
Note on M124: The master control panel is obsolete or not functional.
Note on O124: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on Q124: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on K125: There are individual devices that are not functional.
Note on M125: The master control panel is obsolete or not functional.
Note on O125: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on Q125: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on K126: There are individual devices that are not functional or in regular alarm.
Note on M126: The master control panel is obsolete or not functional.
Note on Q126: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Note on I127: Individual room sensors are failing and require replacement.
Note on M127: The central control panel and software need upgraded.
Note on O127: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system.
Note on Q127: The entire system is in failure and requires replacement of sensors, wiring and central panel
Note on I132: 2-3 pieces of equipment require replacement.
Note on K132: Counters and sinks are not code compliant and require replacement with stainless steel and sink system.
Note on M132: Walk-in cooler and freezer are not functional or function intermittently and require replacement.
Note on O132: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen.
Note on Q132: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Note on I133: 2-3 pieces of equipment require replacement.
Note on M133: Mechanical and electrical service upgrades are required to meet code and amount of program equipment.
Note on O133: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code.
Note on Q133: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Note on E134: Enter total square feet of science classrooms.
Note on K134: Room lacking (and needing) eye wash or fume hood.
Note on M134: Sinks are in disrepair and require replacement.
Note on O134: Work stations need upgrades to meet current program criteria - replace.
Note on Q134: Work stations need upgrades to meet current program criteria - replace
Note on E135: Enter total square feet of art classrooms.
Note on K135: Storage units damaged or in disrepair.
Note on M135: Sinks are in disrepair and require replacement.
Note on O135: Work stations need upgrades to meet current program criteria - replace.
Note on Q135: Work stations need upgrades to meet current program criteria - replace
Note on E136: Insert square feet of auditorium. If multi-purpose room, enter square feet of stage area only. Assumes stage with rigging and lighting.
Note on K136: Seats damaged and need replacement OR sound OR lighting system inadequate and needs upgraded.
Note on M136: Fly rigging in disrepair and needs upgrading.
Note on O136: Two or more stage systems are dysfunctional and need upgrade/replacement.
Note on Q136: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Note on I137: An accessory is damaged or missing.
Note on K137: Accessories need to be replaced to meet ADA.
Note on M137: The stall doors are not functional or missing and need to be replaced.
Note on O137: The restrooms stall structure is failing and needs to be replaced or needs re-configuration.
Note on Q137: The restrooms stall structure is failing or needs re-configuration and needs to be replaced
Note on D138: Note anything specific in the "Other" category at the bottom of the assessment form.
Note on C141: Assume fixed casework (counters, cabinets, shelving, etc.).
Note on I141: The counter top or exposed surface has been damaged and can be refinished.
Note on K141: The drawers and/or doors are damaged and require replacement including hardware.
Note on M141: A combination of minor and moderate action is required, but the cabinet box is still salvageable.
Note on O141: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced.
Note on Q141: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Note on C142: Assume loose furnishings (desks, chairs, tables, etc.).
Note on O142: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement.
Note on Q142: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Note on C148: Paved only or needs to be paved. Apply to square footage of surface area.
Note on E148: Indicate square footage of road.
Note on I148: Minor cracking exists and can be resolved with application of a slurry coat.
Note on M148: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated.
Note on O148: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category should be used.
Note on Q148: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Note on C149: Paved only or needs to be paved. Apply to square footage of surface area.
Note on E149: Indicate square footage of parking lot.
Note on I149: Minor cracking exists and can be resolved with application of a slurry coat.
Note on M149: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated.
Note on O149: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used.
Note on Q149: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Note on C150: Concrete only or needs to be concrete. Apply to square footage of surface area.
Note on E150: Indicate square footage of walks and plazas.
Note on M150: Sections are broken with differential settlement requiring the removal of the effected panels and replacement.
Note on O150: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used.
Note on Q150: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Note on C151: Chain-link fencing. Apply to linear footage of fence.
Note on E151: Indicate length of fencing in feet. Assuming 6-foot high chain-link.
Note on M151: The fence fabric is damaged and needs to be replaced.
Note on O151: The fencing has lost its structural integrity and is beyond repair.
Note on Q151: The fencing has lost its structural integrity and is beyond repair.
Note on C152: Irrigation systems. Other landscape or field items should be included in "Other" category at bottom of assessment form. Apply to square footage of landscape area.
Note on E152: Indicate square footage of landscaped area served (including grass areas).
Note on O152: Irrigation system is dysfunctional and beyond repair.
Note on Q152: Irrigation system is dysfunctional and beyond repair
Note on D154: Assumes 4" line to building. Wells should be placed in "Other" category at bottom of form. Apply to surface area.
Note on O154: A portion of the line has lost its structural integrity and requires replacement.
Note on Q154: A portion of the line has lost its structural integrity and requires replacement
Note on D155: Assumes 6" line to building. Wells and holding tanks should be placed in "Other" category at bottom of form. Apply to surface area.
Note on O155: A portion of the line has lost its structural integrity and requires replacement.
Note on Q155: A portion of the line has lost its structural integrity and requires replacement
Note on C156: Apply to linear footage of sewer lines. Septic fields, tanks, etc. should be placed in "Other" category at bottom of form.
Note on O156: A portion of the line has lost its structural integrity and requires replacement.
Note on Q156: A portion of the line has lost its structural integrity and requires replacement
Note on C157: Apply to square footage of area to be drained. Assumes underground system. For surface runoff system, apply to "Other" category at bottom of form.
Note on I157: Catch basins have lost their integrity or are out of alignment. Remove catch basin, reset, and realign.
Note on K157: Storm sewer piping is dysfunctional or damaged. Remove and replace.
Note on M157: Detention/retention has failed, but piping and catch basins are functional. Replace detention/retention system.
Note on O157: The entire underground system has failed and requires removal and replacement of all components.
Note on Q157: The entire underground system has failed and requires removal and replacement of all components
Note on C158: Apply to linear footage of heating ducts.
Note on O158: A portion of the line has lost its structural integrity and requires replacement.
Note on Q158: A portion of the line has lost its structural integrity and requires replacement
Note on C159: Apply to linear footage of duct work.
Note on O159: A portion of the line has lost its structural integrity and requires replacement.
Note on Q159: A portion of the line has lost its structural integrity and requires replacement
Note on C160: Apply to linear footage of natural gas lines.
Note on O160: A portion of the line has lost its structural integrity and requires replacement.
Note on Q160: A portion of the line has lost its structural integrity and requires replacement
Note on D163: Assumes the private portion of the service lines typically underground after the meter or transformer. Apply to square footage of the whole project site.
Note on M163: The transformer no longer functions and is in need of replacement.
Note on O163: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines.
Note on Q163: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Note on D164: Apply to generator quantity.
Note on I164: The generator needs to be tuned up.
Note on K164: The valves or other engine parts need to be repaired or replaced and then a tune up.
Note on M164: Generator is non-functional or under-sized.
Note on O164: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized.
Note on Q164: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized
Note on C165: Apply to square footage of the whole project site.
Note on K165: The fixtures are nonfunctional and require replacement.
Note on O165: The fixtures, supports, and underground wiring need to be replaced.
Note on Q165: The fixtures, supports, and underground wiring need to be replaced
Note on C166: Assumes low voltage lines underground. Apply to square footage of the whole project site.
Note on O166: Site cabling is inadequate or service is interrupted - replace cabling.
Note on Q166: Site cabling is inadequate or service is interrupted - replace cabling
Note on C170: For assessment professional to hand enter for specialty items and systems that do not fit into categories above.

## Security
District Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Site Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building ID: |  | (autofill) | (autofill) | (autofill) | (autofill)
Date of Assessment: |  | (autofill) | 0/0/0000 | 0/0/0000 | 0/0/0000
SCHOOL SAFETY ASSESSMENT
|  | YES | NO | N/A | COMMENTS
1 | School grounds are fenced.
2 | There is one clearly marked and designated entrance for visitors.
3 | Signs are posted for visitors to report to main office through a designated entrance.
4 | Restricted areas are clearly marked.
5 | Shrubs and foliage are trimmed to allow for good line of sight. (3'-0"/8'- 0" rule)
6 | Shrubs near building have been trimmed "up" to allow view of bottom of building.
7 | Bus loading and drop-off zones are clearly defined.
8 | There is a schedule for maintenance of:
a. Outside lights
b. Locks/Hardware
c. Storage Sheds
d. Windows
e. Other exterior buildings
9 | Parent drop-off and pick-up area is clearly defined.
10 | There is adequate lighting around the building.
11 | Lighting is provided at entrances and other points of possible intrusion.
12 | The school ground is free from trash or debris.
13 | The school is free of graffiti.
14 | Play areas are fenced.
15 | Playground equipment has tamper-proof fasteners.
16 | Visual surveillance of bicycle racks from main office is possible.
17 | Visual surveillance of parking lots from main office is possible.
18 | Parking lot is lighted properly and all lights are functioning.
19 | Accessible lenses are protected by some unbreakable material.
20 | Staff and visitor parking has been designated.
21 | Outside hardware has been removed from all doors except at points of entry.
22 | Ground floor windows:
a. have no broken panes;
b. have locking hardware that is in working order.
23 | Basement windows are protected with grill or well cover.
24 | Doors are locked when classrooms are vacant.
25 | High-risk areas are protected by high security locks and an alarm system:
a. Main office
b. Cafeteria
c. Computer labs
d. Industrial arts rooms
e. Science labs
f. Nurses office
g. Boiler room
h. Electrical rooms
i. Phone line access closet
26 | Unused areas of the school can be closed off during after school activities.
27 | There is two-way communication between the main office and:
a. Classrooms
b. Duty stations
c. Re-locatable classrooms
d. Staff and faculty outside building
e. Buses
28 | There is a central alarm system in the school. If yes, briefly describe in Comments.
29 | The main entrance is visible from the main office.

## ADA
District Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Site Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building ID: |  | (autofill) | (autofill) | (autofill) | (autofill)
Date of Assessment: |  | (autofill) | 0/0/0000 | 0/0/0000 | 0/0/0000
ADA ASSESSMENT
|  | YES | NO | N/A | COMMENTS
1 | There is at least 1 route from site arrival points that does not require the use of stairs.
2 | If parking is provided for the public, there are an adequate number of accessible spaces provided (1 per 25).
3 | There is at least 1 van accessible parking space among the accessible spaces.
4 | The slope of the accessible parking spaces and access aisles is no steeper than 1:48 in all directions.
5 | The access aisles adjoin an accessible route.
6 | Accessible spaces are identified with a sign that includes the International Symbol of Accessibility.
7 | There are signs reading "van accessible" at van accessible spaces.
8 | If the accessible route crosses a curb, there is a curb ramp.
9 | Ramps are sloped no greater than 1:12.
10 | The main entrance is accessible.
11 | If the main entrance is not accessible, there is an alternative accessible entrance.
12 | The alternative accessible entrance can be used independently and during the same hours as the main entrance.
13 | All inaccessible entrances have signs with the International Symbol of Accessibility indicating the location of the nearest accessible entrance.
14 | The door is equipped with hardware, including locks, that is operable with one hand and does not require tight grasping, pinching, or twisting of the wrist.
15 | The operable parts of the door hardware are no less than 34" and no greater than 48" above the floor or ground surface.
16 | In locker rooms, there is at least one room with a bench.
17 | At least one toilet room is accessible (either one for each sex or one unisex).
18 | There are signs with the International Symbol of Accessibility at inaccessible toilet rooms that give directions to accessible toilet rooms.
19 | There is a route to the accessible toilet room(s) that does not include stairs.
20 | The door can be opened easily (5 lbs. maximum force).
21 | Lighting controls are operable with one hand and without tight grasping, pinching, or twisting of the wrist.
22 | Mounted switches are no less than 34" and no greater than 48" above the floor or ground surface.

## IT
District Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Site Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building ID: |  | (autofill) | (autofill) | (autofill) | (autofill)
Date of Assessment: |  | (autofill) | 0/0/0000 | 0/0/0000 | 0/0/0000
INFORMATION TECHNOLOGY ASSESSMENT
|  | YES | NO | N/A | COMMENTS
1 | Connectivity "speed" to the Facility – measured by Megabytes per second (Mbps):
a. 10,000 Mbps or greater
b. 1,000 to 9,999 Mbps
c. 100 to 999 Mbps
d. 10 to 99 Mbps
e. 1 to 9 Mbps
2 | Local area network connectivity "speed" at the individual building level:
a. 10,000 Mbps or greater
b. 1,000 to 9,999 Mbps
c. 100 to 999 Mbps
d. 10 to 99 Mbps
e. 1 to 9 Mbps
3 | Wireless Coverage:
a. Facility-wide
b. Secure?
c. Type:
i. AC wireless router
ii. N wireless router
iii. A/B/G wireless router
4 | Building cabling:
a. Fiber (to the desktop)
b. CAT 6
c. CAT 5 E
d. CAT 5
5 | Security:
a. Access control
b. Video Surveillance
c. Central Communications Systems

## Harmful Substances
District Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Site Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building ID: |  | (autofill) | (autofill) | (autofill) | (autofill)
Date of Assessment: |  | (autofill) | 0/0/0000 | 0/0/0000 | 0/0/0000
HARMFUL SUBSTANCES ASSESSMENT
|  | YES | NO | N/A | COMMENTS
1 | Lead
Has your facility been assessed for lead? If so when?
Is there lead in your facility?
Is lead abatement included in your future bond plans?
2 | Asbestos
Has your facility been assessed for asbestos? If so when?
Is there asbestos in your facility?
Is asbestos abatement included in your future bond plans?
3 | Mold
Has your facility been assessed for mold? If so when?
Is there mold in your facility?
Is mold abatement included in your future bond plans?
4 | Water Quality
Has your facility been assessed for water quality (lead, etc.)? If so when?
Is there a water quality concern in your facility?
Is water treatment included in your future bond plans?
5 | Polychlorinated Biphenyls (PCBs)
Has your facility been assessed for PCBs? If so when?
Are there PCBs in your facility?
Is PCB abatement included in your future bond plans?
6 | Radon
Has your facility been tested for radon? If so when?
Are there elevated levels of radon (above 4 pCi/L) in your facility?
Is radon mitigation included in your future bond plans?

## IAQ
District Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Site Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building Name: |  | (autofill) | (autofill) | (autofill) | (autofill)
Building ID: |  | (autofill) | (autofill) | (autofill) | (autofill)
Date of Assessment: |  | (autofill) | 0/0/0000 | 0/0/0000 | 0/0/0000
INDOOR AIR QUALITY ASSESSMENT
|  | YES | NO | N/A | COMMENTS
1 | Is someone designated to develop and implement an indoor air quality management plan for your school district?
2 | Does your district have an indoor air quality management plan that includes steps for preventing and resolving indoor air quality problems?
3 | Are school buildings inspected once or twice each year for conditions that may lead to indoor air quality problems?
4 | Is a preventive maintenance schedule established and in operation for the heating, ventilation, and air conditioning (HVAC) system? Is the schedule in accordance with the manufacturer's recommendations or accepted practice for the HVAC system?
5 | Does the HVAC preventive maintenance schedule include checking and/or changing air filters and belts, lubricating equipment parts, checking the motors, and confirming that all equipment is in operating order?
6 | Is the maintenance schedule updated to show all maintenance performed on the building systems?
7 | Does the maintenance schedule include the dates that the building systems maintenance was performed and the names of the persons or companies performing the work?
8 | Are maintenance schedules retained for at least three years?
9 | Are damaged or inoperable components of the HVAC system replaced or repaired as appropriate?
10 | Are reservoirs or parts of the HVAC system with standing water checked visually for microbial growth?
11 | Are water leaks that could promote the growth of biological agents promptly repaired?
12 | Are damp or wet materials that could promote the growth of biological agents promptly dried, replaced, removed, or cleaned?
13 | Are microbial contaminants removed from ductwork, humidifiers, other HVAC and building system components, and from building surfaces such as carpeting and ceiling tiles when found during regular or emergency maintenance activities or visual inspection?
14 | Is general or local exhaust ventilation used where housekeeping and maintenance activities could reasonably be expected to result in exposure to hazardous substances above applicable exposure limits?
15 | Does the HVAC system have CO2 monitoring capability (demand control ventilation)?
16 | Are humidity levels maintained between 30% to 60% relative humidity?
17 | When a contaminant is identified in the make-up air supply, is the source of the contaminant eliminated, or are the make-up inlets or exhaust air outlets relocated to avoid entry of the contaminant into the air system?
18 | If buildings do not have mechanical ventilation, are windows, doors, vents, stacks, and other portals used for natural ventilation operating properly?

## PCA Cost Tables - READ ONLY
District Name: |  | 0 | State Assigned Inflation Factor |  |  | #VALUE! | Inflation to projected mid-point of Construction Period
Site Name: |  | 0 | State Assigned Soft Development Factor |  |  | 1.38 | Assuming design, direct-hire specialists (envelope, commissioning, cost estimating, etc.), state solar, permits, survey, geo, bond issuance, management, furnishings, and 15% contingency
Building Name: |  | 0 | Yearly Escalation Beyond Dates Below |  |  | 1.05 | Inflation Rate Per Annum for Projects commencing further than projected construction mid-point.
Building ID: |  | 0
|  | *The values below are escalated to the date of assessment |  | LEVEL OF ACTION
Level 1 | Level 2 | Level 3 | Type (as applicable) |  | Minor |  | Moderate |  | Major |  | Replace as Part of Renovation |  | Replace as singular scope | Forwarded Unit Budget | Cost Estimator Notes
A SUBSTRUCTURE
A10 Foundations
|  | A1010 Standard Foundations |  | #VALUE! | Minor |  | Moderate | #VALUE! | Major |  | Replace |  | Replace | 0
|  | A1020 Special Foundations |  | #VALUE! | Minor |  | Moderate | #VALUE! | Major |  | Replace |  | Replace | 0
|  | A1030 Slab on Grade |  |  | Minor | #VALUE! | Moderate | #VALUE! | Major |  | Replace |  | Replace | 0
A20 Basement Construction
|  | A2010 Basement Excavation | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
|  | A2020 Basement Walls |  | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major |  | Replace |  | Replace | 0
B SHELL
B10 Superstructure
|  | B1010 Floor Construction | Wood |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 113 | Replace | 0
|  |  | Steel |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 117 | Replace | 0
|  |  | Concrete |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 123 | Replace | 0
|  | B1020 Roof Construction | Wood |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 88 | Replace | 0
|  |  | Steel |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 92 | Replace | 0
|  |  | Concrete |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 99 | Replace | 0
B20 Exterior Enclosure
|  | B2010 Exterior Walls | Concrete Formed / Tilt |  | Minor | #VALUE! | Moderate | #VALUE! | Major |  | Replace |  | Replace | 0
|  |  | Masonry |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 37.73 | Replace | 0
|  |  | Framed w/ Wood Siding |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 30.51 | Replace | 0
|  |  | Framed w/ Metal Panel |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 35.51 | Replace | 0
|  |  | Framed w/Stucco |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 35.69 | Replace | 0
|  |  | Framed w/Masonry Veneer |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 43.61 | Replace | 0
|  | B2020 Exterior Windows | Wood |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 11.3 | Replace | 0
|  |  | Aluminum |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 12 | Replace | 0
|  |  | Clad |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 11.5 | Replace | 0
|  |  | Curtain Wall |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 30 | Replace | 0
|  | B2030 Exterior Doors | Wood |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 2000 | Replace | 0 | Per leaf
|  |  | Hollow Metal |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 1800 | Replace | 0 | Per leaf
|  |  | Storefront |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 3000 | Replace | 0 | Per leaf
B30 Roofing
|  | B3010 Roof Coverings | Asphalt Shingle | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 15 | Replace | 0
|  |  | Built-Up | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 26 | Replace | 0
|  |  | Single Ply | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 24 | Replace | 0
|  |  | Metal |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 32 | Replace | 0
|  |  | Concrete Tile |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 34 | Replace | 0
|  | B3020 Roof Openings | Skylights |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 4.78 | Replace | 0 | By Building GFA
|  |  | Access Hatch |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 0.33 | Replace | 0 | Per hatch
C INTERIORS
C10 Interior Construction
|  | C1010 Partitions | Framed |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 50.68 | Replace | 0
|  |  | Masonry |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 64.18 | Replace | 0
|  | C1020 Interior Doors | Wood |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 1800 | Replace | 0 | Per leaf
|  |  | Hollow Metal |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 1600 | Replace | 0 | Per leaf
|  | C1030 Fittings | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
C20 Stairs
|  | C2010 Stair Construction | Wood |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 2.34 | Replace | 0 | Cost/Flight
|  |  | Metal | #VALUE! | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 2.4 | Replace | 0 | Cost/Flight
|  |  | Concrete |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 4.92 | Replace | 0 | Cost/Flight
|  | C2020 Stair Finishes | Concrete Fill | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 1.96 | Replace | 0 | Cost/Flight
|  |  | Resilient |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 1.5 | Replace | 0 | Cost/Flight
C30 Interior Finishes
|  | C3010 Wall Finishes | Paint on Masonry | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 5.37 | Replace | 0
|  |  | Wallboard | #VALUE! | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 9.06 | Replace | 0
|  |  | Wainscot | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 2.34 | Replace | 0
|  |  | Ceramic Tile | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 3.43 | Replace | 0
|  | C3020 Floor Finishes | Carpet / Soft Surface |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 8.68 | Replace | 0
|  |  | Resilient Tile | #VALUE! | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 8.8 | Replace | 0
|  |  | Resilient Sheet |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 14 | Replace | 0
|  |  | Polished Concrete | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 11 | Replace | 0
|  |  | Ceramic Tile | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 27.14 | Replace | 0
|  |  | Liquid Applied |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 16.11 | Replace | 0
|  |  | Wood Sports Floor |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 20 | Replace | 0
|  | C3030 Ceiling Finishes | Wallboard | #VALUE! | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 14 | Replace | 0
|  |  | Lay-In Ceiling Tile | #VALUE! | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 10 | Replace | 0
|  |  | Glued-Up Ceiling Tile | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 6.74 | Replace | 0
|  |  | Painted Structure |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 5.21 | Replace | 0
D SERVICES
D10 Conveying
|  | D1010 Elevators & Lifts |  | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 60000 | Replace | 0 | Per stop
|  | D1020 Escalators & Moving Walks |  |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 120000 | Replace | 0
|  | D1090 Other Conveying Systems |  |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 30000 | Replace | 0
D20 Plumbing
|  | D2010 Plumbing Fixtures |  |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 75.38 | Replace | 0 | Cost/SF of building GFA
|  | D2020 Domestic Water Distribution |  | #VALUE! | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 77.38 | Replace | 0
|  | D2030 Sanitary Waste |  | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 72.07 | Replace | 0
|  | D2040 Rain Water Drainage |  |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 72.35 | Replace | 0
|  | D2090 Other Plumbing Systems | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
D30 HVAC
|  | D3010 Energy Supply |  | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 12.74 | Replace | 0 | Cost/SF of building GFA
|  | D3020 Heat Generating Systems | Boiler | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 9.52 | Replace | 0 | Cost/SF of building GFA
|  |  | Air Handler |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 5.82 | Replace | 0 | Cost/SF of building GFA
|  |  | Furnace |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 4.26 | Replace | 0 | Cost/SF of building GFA
|  |  | Heat Exchanger |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 2.02 | Replace | 0 | Cost/SF of building GFA
|  | D3030 Cooling Generating Systems | Component of air handler |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 3.86 | Replace | 0 | Cost/SF of building GFA
|  |  | Stand alone chiller |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 5.54 | Replace | 0 | Cost/SF of building GFA
|  | D3040 Distribution Systems | Ductwork |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 35.15 | Replace | 0 | Cost/SF of building GFA
|  |  | Hot water return & supply | #VALUE! | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 35.15 | Replace | 0 | Cost/SF of building GFA
|  | D3050 Terminal & Package Units | Above ceiling VAV unit | . | Minor |  | Moderate |  | Major | #VALUE! | Replace | 16.03 | Replace | 0 | Cost/SF of building GFA
|  |  | In-room ventilator unit |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 27.96 | Replace | 0 | Cost/SF of building GFA
|  |  | In-room radiant unit | #VALUE! | Minor |  | Moderate |  | Major | #VALUE! | Replace | 15.14 | Replace | 0 | Cost/SF of building GFA
|  | D3060 Controls & Instrumentation |  |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 14.69 | Replace | 0 | Cost/SF of building GFA
|  | D3070 Systems Testing & Balancing |  |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 1.46 | Replace | 0 | Cost/SF of building GFA
|  | D3090 Other HVAC Systems & Equipment | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
D40 Fire Protection
|  | D4010 Sprinklers |  |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 18.64 | Replace | 0
|  | D4020 Standpipes |  |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 10.24 | Replace | 0
|  | D4030 Fire Protection Specialties |  |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 48.15 | Replace | 0
|  | D4090 Other Fire Protection Systems | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
D50 Electrical
|  | D5010 Electrical Service & Distribution |  |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 18.11 | Replace | 0
|  | D5020 Lighting and Branch Wiring |  |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 37.95 | Replace | 0
|  | D5030 Communications & Security | Voice / Data System |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 18.64 | Replace | 0
|  |  | Clock / Intercom System |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 2 | Replace | 0
|  |  | Closed Circuit Surveillance |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 2.23 | Replace | 0
|  |  | Access Control System |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 2 | Replace | 0
|  |  | Intrusion Alarm System |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 1.5 | Replace | 0
|  |  | Fire Alarm / Detection |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 4.25 | Replace | 0
|  |  | Lighting Control System | #VALUE! | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 1.6 | Replace | 0
|  | D5090 Other Electrical Systems | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
E EQUIPMENT & FURNISHINGS
E10 Equipment
|  | E1010 Commercial Equipment | Food Service | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 2.85 | Replace | 0
|  |  | Vocational | #VALUE! | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 2.66 | Replace | 0
|  | E1020 Institutional Equipment | Science |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 4.46 | Replace | 0
|  |  | Art |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 4.31 | Replace | 0
|  |  | Stage Performance |  | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 35000 | Replace | 0 | Cost/SF of Stage Performance Area
|  |  | Restroom Accessories/Stalls | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 1.48 | Replace | 0
|  | E1030 Vehicular Equipment | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
|  | E1090 Other Equipment | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
E20 Furnishings
|  | E2010 Fixed Furnishings |  | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 16.32 | Replace | 0
|  | E2020 Movable Furnishings |  |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 24 | Replace | 0
F SPECIAL CONSTRUCTION & DEMOLITION - NOT USED
G BUILDING SITE WORK
| G10 Site Preparation |  | NOT USED
G20 Site Improvements
|  | G2010 Roadways |  | #VALUE! | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 8 | Replace | 0 | Cost/SF of surface area
|  | G2020 Parking Lots |  | #VALUE! | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 8 | Replace | 0 | Cost/SF of surface area
|  | G2030 Pedestrian Paving |  |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 11 | Replace | 0 | Cost/SF of surface area
|  | G2040 Site Development |  |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 35 | Replace | 0 | Cost/LF of fencing
|  | G2050 Landscaping |  |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 2.5 | Replace | 0 | Cost/SF of irrigated area
G30 Site Mechanical Utilities
|  | G3010 Water Supply | Domestic |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 65 | Replace | 0 | Cost/LF of pipe
|  |  | Fire |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 65 | Replace | 0 | Cost/LF of pipe
|  | G3020 Sanitary Sewer |  |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 45 | Replace | 0 | Cost/LF of pipe
|  | G3030 Storm Sewer |  | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 2.46 | Replace | 0 | Cost/SF of area to be drained
|  | G3040 Heating Distribution |  |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 225 | Replace | 0 | Cost/LF of HHW/Steam piping
|  | G3050 Cooling Distribution |  |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 225 | Replace | 0 | Cost/LF of CHW piping
|  | G3060 Fuel Distribution |  |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 35 | Replace | 0 | Cost/LF of gas piping
|  | G3090 Other Site Mechanical Utilities | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
G40 Site Electrical Utilities
|  | G4010 Electrical Distribution | Service |  | Minor |  | Moderate | #VALUE! | Major | #VALUE! | Replace | 2.48 | Replace | 0
|  |  | Generator | #VALUE! | Minor | #VALUE! | Moderate | #VALUE! | Major | #VALUE! | Replace | 30000 | Replace | 0 | Cost/occurrence
|  | G4020 Site Lighting |  |  | Minor | #VALUE! | Moderate |  | Major | #VALUE! | Replace | 1.3 | Replace | 0
|  | G4030 Site Communications & Security |  |  | Minor |  | Moderate |  | Major | #VALUE! | Replace | 0.8 | Replace | 0
|  | G4090 Other Site Electrical Utilities | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace |  | Replace | 0
| G90 Other Site Construction |  | NOT USED
Ability to enter one-off items for site specific scope
Note on C10: Standard spread and strip / perimeter footings
Note on E10: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on I10: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation.
Note on C11: Pilings or other extended foundation systems that overcome non-standard soil conditions.
Note on E11: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on I11: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation.
Note on C12: Standard ground-set concrete slab. If slab is elevated (i.e. has a crawl space or basement), apply conditions to B1010 instead.
Note on G12: Separation cracks occurring requiring route and fill and patch
Note on I12: Differential settlement occurring - requires removal of section of slab, adjustment to sub-grade, and new infill.
Note on C15: Assumed as concrete walls with water-proofing on the exterior. Includes only the structural portion and not the wall finishes.
Note on E15: Inadequate below grade venting is observed - cut in and add venting
Note on G15: Wall is cracked and spalling requiring route and fill and patch and re-finish.
Note on I15: Wall is cracked with evidence of water intrusion. Repairs to be implemented and water barrier to be applied.
Note on C18: A suspended floor including the structural members and floor construction, but not including the actual finish.
Note on G18: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on K18: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on M18: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on G19: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on K19: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on M19: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on G20: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on K20: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on M20: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on C21: The roof structure referring to the supporting structure and the deck but excluding the roofing itself.
Note on I21: Evidence of a spongy decking from water intrusion - replacing the deck but not the trusses.
Note on K21: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on M21: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on I22: Evidence of a flexing decking from water intrusion / rust - replacing the deck but not the trusses.
Note on K22: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on M22: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on I23: Evidence of a spongy / spalling deck from water intrusion - replacing the deck but not the beams.
Note on K23: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on M23: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on G25: Surface is in tact, but finish is deteriorated - paint.
Note on I25: Cracks visible - route and patch prior to painting.
Note on G26: Surface is in tact, but finish is deteriorated - paint.
Note on I26: Some blocks are damaged, needing patch and repair prior to sealing or painting.
Note on K26: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on M26: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on G27: Surface is in tact, but finish is deteriorated - paint.
Note on I27: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on K27: The panels are lifting or separating or otherwise losing their integrity - remove and replace.
Note on M27: The panels are lifting or separating or otherwise losing their integrity - remove and replace
Note on G29: Surface is in tact, but finish is deteriorated - paint.
Note on I29: Cracks visible - route and patch prior to painting.
Note on K29: System in failure with evidence of water intrusion - remove and replace.
Note on M29: System in failure with evidence of water intrusion - remove and replace
Note on G30: Minor repairs needed to mortar, prep, and re-sealing.
Note on I30: Mortar missing in a majority of areas requiring complete re-pointing and sealing.
Note on K30: Masonry visibly damaged and requiring removal and replacement.
Note on M30: Masonry visibly damaged and requiring removal and replacement
Note on G31: The glazing is double pane, but is broken or fogged and requires replacement.
Note on I31: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on K31: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on M31: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D32: This assumes both individual aluminum windows and storefront systems.
Note on G32: The glazing is double pane, but is broken or fogged and requires replacement.
Note on I32: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on K32: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on M32: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D33: This assumes a metal windows system clad with wood or vinyl.
Note on G33: The glazing is double pane, but is broken or fogged and requires replacement.
Note on I33: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on K33: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on M33: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on G34: Minor leaks at wall seams - re-caulk and re-seal.
Note on I34: Window panels fogged and require replacement.
Note on K34: Settlement or displacement is evident.
Note on M34: Settlement or displacement is evident
Note on G35: Door hardware is damaged or non-functional and requires replacement.
Note on I35: Door panel and hardware are damaged and require replacement.
Note on K35: Door frame, door, and hardware are damaged and require replacement.
Note on M35: Door frame, door, and hardware are damaged and require replacement
Note on G36: Door hardware is damaged or non-functional and requires replacement.
Note on I36: Door panel and hardware are damaged and require replacement.
Note on K36: Door frame, door, and hardware are damaged and require replacement.
Note on M36: Door frame, door, and hardware are damaged and require replacement
Note on G37: Door hardware is damaged or non-functional and requires replacement.
Note on I37: Door panel and hardware are damaged and require replacement.
Note on K37: Door frame, door, and hardware are damaged and require replacement.
Note on M37: Door frame, door, and hardware are damaged and require replacement
Note on C39: Assumes the insulation, roof covering, and associated flashings, gutters, and downspouts.
Note on E39: Small number of shingles lifting and/or separation in a portion of flashing
Note on G39: Leaks in a specific area or zone related to poor detailing and / or flashing.
Note on I39: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING.
Note on K39: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system.
Note on M39: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on E40: Minor blistering requiring isolated patches
Note on G40: Leaks in a specific area or zone related to poor detailing and / or flashing or unchecked blisters.
Note on I40: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING.
Note on K40: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system.
Note on M40: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on E41: Minor blistering requiring isolated patches
Note on G41: Leaks in a specific area or zone related to poor detailing and / or flashing or seam separation.
Note on I41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Prep and re-coat roof system OVER TOP OF EXISTING.
Note on K41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system.
Note on M41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on G42: Leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing and sealant.
Note on K42: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing.
Note on M42: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Note on G43: Leaks occurring at isolated areas requiring grout removal and re-grout at isolated tile locations.
Note on K43: Tiles are cracked, loose, or damaged and require removal and replacement.
Note on M43: Tiles are cracked, loose, or damaged and require removal and replacement
Note on G44: Minor leaking is occurring, requiring re-caulk and re-seal.
Note on K44: The panes or framing are damaged beyond repair and requires replacement.
Note on M44: The panes or framing are damaged beyond repair and requires replacement
Note on K45: The door is non-functional or damaged beyond repair and requires replacement.
Note on M45: The door is non-functional or damaged beyond repair and requires replacement
Note on K48: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on M48: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on I49: There are some blocks that are damaged and requires a strategic removal and replacement.
Note on K49: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on M49: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on G50: Door hardware is damaged or non-functional and requires replacement.
Note on I50: Door panel and hardware are damaged and require replacement.
Note on K50: Door frame, door, and hardware are damaged and require replacement.
Note on M50: Door frame, door, and hardware are damaged and require replacement
Note on G51: Door hardware is damaged or non-functional and requires replacement.
Note on I51: Door panel and hardware are damaged and require replacement.
Note on K51: Door frame, door, and hardware are damaged and require replacement.
Note on M51: Door frame, door, and hardware are damaged and require replacement
Note on I54: Rails not compliant with code and require removal and replacement.
Note on K54: Structural integrity of stair unit is compromised and requires its removal and replacement.
Note on M54: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on E55: Rust visible - prep and re-finish.
Note on I55: Rails not compliant with code and require removal and replacement.
Note on K55: Structural integrity of stair unit is compromised and requires its removal and replacement.
Note on M55: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on I56: An isolated structural crack or separation requiring re-enforcement in place.
Note on K56: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit.
Note on M56: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit
Note on E57: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal.
Note on K57: Severe cracking requiring removal and replacement of tread in fills.
Note on M57: Severe cracking requiring removal and replacement of tread in fills
Note on K58: Finish is lifting or separating and creating trip hazards - remove and replace.
Note on M58: finish is lifting or separating and creating trip hazards - remove and replace
Note on E60: Surface is in tact, but finish is deteriorated - paint.
Note on K60: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on M60: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on E61: Surface is in tact, but finish is deteriorated - paint.
Note on G61: Surface is damaged - patching of the surface is required prior to painting.
Note on K61: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on M61: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on E62: Surface is in tact, but finish is deteriorated - paint.
Note on K62: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on M62: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on E63: Grout is damaged or deteriorated.
Note on K63: Tiles are cracked or in disrepair.
Note on M63: Tiles are cracked or in disrepair
Note on K64: Worn or severely stained or starting to pull up / bubble.
Note on M64: worn or severely stained or starting to pull up / bubble
Note on E65: Sporadic number of tiles are lifting or cracked / broken and require replacement.
Note on I65: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are NOT asbestos.
Note on K65: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are asbestos.
Note on M65: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are asbestos
Note on K66: Severely worn or seams separating - replace.
Note on M66: Severely worn or seams separating - replace
Note on E67: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal.
Note on K67: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above.
Note on M67: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above
Note on E68: Grout is damaged or deteriorated.
Note on K68: Tiles are cracked or in disrepair.
Note on M68: Tiles are cracked or in disrepair
Note on K69: Systemic blistering or severely worn traffic areas - strip and replace.
Note on M69: Systemic blistering or severely worn traffic areas - strip and replace
Note on G70: Surface is damaged - requires sanding, repair, and re-coat / re-stripe.
Note on K70: Wood planks are deteriorated, separating, and multiple dead spots - replace floor.
Note on M70: Wood planks are deteriorated, separating, and multiple dead spots - replace floor
Note on E71: Surface is in tact, but finish is deteriorated - paint.
Note on G71: Surface is damaged - patching of the surface is required prior to painting.
Note on K71: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on M71: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on E72: Stained or damaged ceiling tiles.
Note on G72: Diagonal bracing missing from grid.
Note on K72: Grid is sagging with tiles compromised - requires replacement of system.
Note on M72: Grid is sagging with tiles compromised - requires replacement of system
Note on E73: Stained or damaged ceiling tiles.
Note on K73: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on M73: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on K74: Surface is in tact, but finish is deteriorated - paint.
Note on M74: Surface is in tact but finish is deteriorated - paint
Note on C77: Assume standard cab-style elevator.
Note on E77: The elevator doors are damaged and require replacement.
Note on G77: Electrical components are not working.
Note on I77: Replacement of the hoist cables, guide rails, or other similar mechanical components is required.
Note on K77: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on M77: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on G78: Electrical components are not working.
Note on K78: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on M78: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C79: Assume open vertical or inclined lift.
Note on G79: Electrical components are not working.
Note on K79: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on M79: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C81: All fixtures (toilets, urinals, sinks, showers, etc.) to be lumped together here.
Note on G81: Flush valves or faucets are non-functional and require replacement.
Note on K81: The fixture itself is broken or is not compliant with water efficiency standards.
Note on M81: The fixture itself is broken or is not compliant with water efficiency standards
Note on E82: The vale stems, pressure gauges, and gate valves no longer function.
Note on G82: The insulation on the piping is in disrepair, loose, or missing.
Note on K82: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on M82: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on E83: In some areas, there are back ups requiring the replacement of the broken floor or wall, clean outs, routing and cleaning the problem areas, and snaking floor drains.
Note on K83: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement.
Note on M83: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Note on C84: This is for the presence of interior rain drains; note building percentage based on area of roof served - excludes external downspouts.
Note on G84: The rain drain or overflow is damaged and needs replacement.
Note on K84: The integrity of the piping is compromised and is leaking inside the walls.
Note on M84: The integrity of the piping is compromised and is leaking inside the walls
Note on C87: This assumes gas piping.
Note on E87: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on K87: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on M87: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on E88: The burner is inefficient and requires refurbishment.
Note on G88: One major component needs to be replaced.
Note on I88: More than one major component needs to be replaced.
Note on K88: The system is in failure.
Note on M88: The system is in failure
Note on I89: Some of the distribution fans and coils are dysfunctional.
Note on K89: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair.
Note on M89: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on G90: A small number of minor parts need to be repaired or replaced.
Note on I90: The burner, combustion chamber, or fan are faulty and require replacement.
Note on K90: The entire furnace requires replacement.
Note on M90: The entire furnace requires replacement
Note on G91: A small number of minor parts need to be repaired or replaced.
Note on I91: System operating at low efficiency; shell exhibits corrosion. Retube heat exchanger.
Note on K91: System operates at low efficiency with corrosion and leaks apparent. Replace system.
Note on M91: System operates at low efficiency with corrosion and leaks apparent. Replace system
Note on I92: Some of the distribution fans and coils are dysfunctional.
Note on K92: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair.
Note on M92: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on K93: The chiller is beyond economic repair.
Note on M93: The chiller is beyond economic repair
Note on G94: Dampers in the system are inoperative.
Note on I94: The insulation is damaged or missing.
Note on K94: The ductwork is damaged or inadequately designed and requires replacement.
Note on M94: The ductwork is damaged or inadequately designed and requires replacement
Note on E95: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on G95: The insulation on the piping is in disrepair, loose, or missing.
Note on K95: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on M95: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on K96: Entire unit is failing to function.
Note on M96: Entire unit is failing to function
Note on G97: Internal compressor is bad and requires replacement.
Note on K97: Entire unit is failing to function.
Note on M97: Entire unit is failing to function
Note on E98: In-room valve is failing and requires replacement.
Note on K98: Entire unit is failing to function.
Note on M98: Entire unit is failing to function
Note on I99: Some of the sensors or valve actuators are dysfunctional. Replace these sensors or actuators.
Note on K99: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system - replace.
Note on M99: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system - replace
Note on K100: One or more zones require re-balancing.
Note on M100: One or more zones require re-balancing
Note on G103: Sprinkler heads are inoperable or non-compliant and need to be replaced.
Note on K103: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads.
Note on M103: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads
Note on G104: The Siamese twin connection, tamper flow switches, or flow control valves are inoperable and need to be replaced.
Note on K104: The fire pump is beyond repair and needs to be replaced.
Note on M104: The fire pump is beyond repair and needs to be replaced
Note on C105: Assume chemical extinguishing system.
Note on G105: The back-up tank has been discharged or lacks pressure and needs to be replaced.
Note on K105: The system is non-functional or not compliant with the current needs and needs to be replaced.
Note on M105: The system is non-functional or not compliant with the current needs and needs to be replaced
Note on G108: Wiring has systemic problems or does not meet code and needs to be replaced.
Note on I108: Branch panels are obsolete with replacement breakers difficult to acquire and requires replacement.
Note on K108: Main switchgear is obsolete or undersized and requires replacement, including service into building.
Note on M108: Main switchgear is obsolete or undersized and requires replacement, including service into building
Note on I109: The lighting fixtures are obsolete or non-functional and require replacement.
Note on K109: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring.
Note on M109: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring
Note on G110: There are individual devices that are not functional.
Note on I110: The master control panel is obsolete or not functional.
Note on K110: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on M110: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G111: There are individual devices that are not functional.
Note on I111: The master control panel is obsolete or not functional.
Note on K111: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on M111: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G112: There are individual devices that are not functional.
Note on I112: The master control panel is obsolete or not functional.
Note on K112: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on M112: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G113: There are individual devices that are not functional.
Note on I113: The master control panel is obsolete or not functional.
Note on K113: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on M113: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G114: There are individual devices that are not functional.
Note on I114: The master control panel is obsolete or not functional.
Note on K114: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on M114: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G115: There are individual devices that are not functional or in regular alarm.
Note on I115: The master control panel is obsolete or not functional.
Note on K115: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system.
Note on M115: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Note on E116: Individual room sensors are failing and require replacement.
Note on I116: The central control panel and software need upgrading.
Note on K116: The entire system is in failure and requires replacement of sensors, wiring and central panel.
Note on M116: The entire system is in failure and requires replacement of sensors, wiring and central panel
Note on E121: 2-3 pieces of equipment require replacement.
Note on G121: Counters and sinks are not code compliant and require replacement with stainless steel and sink system.
Note on I121: Walk-in cooler and freezer are not functional or function intermittently and require replacement.
Note on K121: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen.
Note on M121: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Note on E122: 2-3 pieces of equipment require replacement.
Note on I122: Mechanical and electrical service upgrades are required to meet code and amount of program equipment.
Note on K122: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code.
Note on M122: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Note on G123: Room lacking (and needing) eye wash or fume hood.
Note on I123: Sinks are in disrepair and require replacement.
Note on K123: Work stations need upgrades to meet current program criteria - replace.
Note on M123: Work stations need upgrades to meet current program criteria - replace
Note on G124: Storage units damaged or in disrepair.
Note on I124: Sinks are in disrepair and require replacement.
Note on K124: Work stations need upgrades to meet current program criteria - replace.
Note on M124: Work stations need upgrades to meet current program criteria - replace
Note on G125: Seats damaged and need replacement OR sound OR lighting system inadequate and needs upgraded.
Note on I125: Fly rigging in disrepair and needs upgrading.
Note on K125: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems.
Note on M125: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Note on E126: An accessory is damaged or missing.
Note on G126: Accessories need to be replaced to meet ADA.
Note on I126: The stall doors are not functional or missing and need to be replaced.
Note on K126: The restrooms stall structure is failing or needs re-configuration and needs to be replaced.
Note on M126: The restrooms stall structure is failing or needs re-configuration and needs to be replaced
Note on D127: Note anything specific in the "Other" category at the bottom of the assessment form.
Note on C130: Assume fixed casework (counters, cabinets, shelving, etc.).
Note on E130: The countertop or exposed surface has been damaged and can be refinished.
Note on G130: The drawers and/or doors are damaged and require replacement including hardware.
Note on I130: A combination of minor and moderate action is required, but the box is still salvageable.
Note on K130: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced.
Note on M130: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Note on C131: Assume loose furnishings (desks, chairs, tables, etc.).
Note on K131: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement.
Note on M131: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Note on C137: Paved only or needs to be paved.
Note on E137: Minor cracking exists and can be resolved with application of a slurry coat.
Note on I137: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated.
Note on K137: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used.
Note on M137: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Note on C138: Paved only or needs to be paved.
Note on E138: Minor cracking exists and can be resolved with application of a slurry coat.
Note on I138: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated.
Note on K138: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used.
Note on M138: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Note on C139: Concrete only or needs to be concrete.
Note on I139: Sections are broken with differential settlement requiring the removal of the effected panels and replacement.
Note on K139: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used.
Note on M139: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Note on C140: Chain-link fencing.
Note on I140: The fence fabric is damaged and needs to be replaced.
Note on K140: The fencing has lost its structural integrity and is beyond repair.
Note on M140: The fencing has lost its structural integrity and is beyond repair.
Note on C141: Irrigation systems. Other landscape or field items should be included in "Other" category at bottom of assessment form.
Note on K141: Irrigation system is dysfunctional and beyond repair.
Note on M141: Irrigation system is dysfunctional and beyond repair
Note on D143: Assumes 4" line to building. Wells should be placed in "Other" category at bottom of form.
Note on K143: A portion of the line has lost its structural integrity and requires replacement.
Note on M143: A portion of the line has lost its structural integrity and requires replacement
Note on D144: Assumes 6" line to building. Wells and holding tanks should be placed in "Other" category at bottom of form.
Note on K144: A portion of the line has lost its structural integrity and requires replacement.
Note on M144: A portion of the line has lost its structural integrity and requires replacement
Note on C145: Lines only. Septic fields, tanks, etc. should be placed in "other" category at bottom of form.
Note on K145: A portion of the line has lost its structural integrity and requires replacement.
Note on M145: A portion of the line has lost its structural integrity and requires replacement
Note on C146: Assumes underground system. For surface runoff system, apply to "Other" category at bottom of form.
Note on E146: Catch basins have lost their integrity or are out of alignment. Remove catch basin, reset, and realign.
Note on G146: Storm sewer piping is dysfunctional or damaged. Remove and replace.
Note on I146: Detention/retention has failed, but piping and catch basins are functional. Replace detention / retention system.
Note on K146: The entire underground system has failed and requires removal and replacement of all components.
Note on M146: The entire underground system has failed and requires removal and replacement of all components
Note on K147: A portion of the line has lost its structural integrity and requires replacement.
Note on M147: A portion of the line has lost its structural integrity and requires replacement
Note on K148: A portion of the line has lost its structural integrity and requires replacement.
Note on M148: A portion of the line has lost its structural integrity and requires replacement
Note on C149: Natural gas lines
Note on K149: A portion of the line has lost its structural integrity and requires replacement.
Note on M149: A portion of the line has lost its structural integrity and requires replacement
Note on D152: Assumes the private portion of the service lines typically underground after the meter or transformer.
Note on I152: The transformer no longer functions and is in need of replacement.
Note on K152: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines.
Note on M152: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Note on E153: The generator needs to be tuned up.
Note on G153: The valves or other engine parts need to be repaired or replaced and then a tune up.
Note on I153: Generator is non-functional or under-sized.
Note on K153: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized.
Note on M153: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized
Note on G154: The fixtures are nonfunctional and require replacement.
Note on K154: The fixtures, supports, and underground wiring need to be replaced.
Note on M154: The fixtures, supports, and underground wiring need to be replaced
Note on C155: Assumes low voltage lines underground.
Note on K155: Site cabling is inadequate or service is interrupted - replace cabling.
Note on M155: Site cabling is inadequate or service is interrupted - replace cabling

## Building Type Budget-READ ONLY
Budgeted Replacement Cost of Buildings by Type
NOTE:
These are building only costs and any site work should be added if required
Escalated to: 11/5/2026
Type | Raw Budget / SF (as of Q1 2023) | Inflated to Construction Midpoint Based on State Rate** | Developed Budget* | Forwarded FCI Budget
Elementary School | 500 | 602.0208 | 830.7888 | 0
Middle School | 525 | 632.1219 | 872.3282 | 0
K-8 School | 550 | 662.2229 | 913.8676 | 0
High School | 600 | 722.425 | 996.9465 | 0
Gymnasium Building | 504.6344 | 607.6009 | 838.4892 | 0
Pool Building | 624.3383 | 751.7293 | 1037.3865 | 0
Vocational Building | 472.948 | 569.4491 | 785.8398 | 0
Administrative Building | 375.5419 | 452.1681 | 623.992 | 0
Maintenance Building | 475.2952 | 572.2752 | 789.7398 | 0
Storage Building | 357.9383 | 430.9726 | 594.7422 | 0
Warehouse | 357.9383 | 430.9726 | 594.7422 | 0
Food Services Building | 557.4449 | 671.1869 | 926.2379 | 0
Bus Shelter | 340.3348 | 409.7773 | 565.4927 | 0
Bus Garage | 357.9383 | 430.9726 | 594.7422 | 0
Athletic Grandstand | 316.8634 | 381.5167 | 526.4931 | 0
Large Greenhouse | 150 | 180.6063 | 249.2366 | 0
Other Commercial | 394.3189 | 474.7764 | 655.1914 | 0
|  |  | FCI Reference | 1
*Developed Budget is based on State Assigned factor on PSA Cost Table Sheet
**Inflation is to projected construction mid-point entered in the Physical Condition Assessment sheet.
Note:
Small, support outbuildings shall be assessed as "other" under the primary building assessment and not as their own building assessment.
Assumed raw budgets are extrapolated from RLB Cost Estimating Guide (escalated where appropriate), National Building Cost Manual, recent public bid results and in-house T&T/CBRE Heery estimates and benchmarking.

## County Cost Factor - READ ONLY
County Cost Factor for Physical Assessment Budget Calculation
Counties | Prevailing Wage Rate Regions | Cost Factor | Forwarded Factor | Historic values | Delta | Notes
Clatsop | 1 | 1.03 | 0 | 1.05 | -0.02 | MEAN AVG SPLIT BETWEEN MULTNOMAH/POLK/LANE
Columbia | 1 | 1.03 | 0 | 1.05 | -0.02 | See above
Tillamook | 1 | 1.03 | 0 | 1.05 | -0.02 | See above
Clackamas | 2 | 1.11 | 0 | 1.13 | -0.02 | See below
Multnomah | 2 | 1.11 | 0 | 1.13 | -0.02 | Portland, per NATIONAL BUILDING COST MANUAL 2023
Washington | 2 | 1.11 | 0 | 1.13 | -0.02 | See above
Marion | 3 | 0.99 | 0 | 1 | -0.01 | Salem, per NATIONAL BUILDING COST MANUAL 2023
Polk | 3 | 0.99 | 0 | 1 | -0.01 | See above
Yamhill | 3 | 0.99 | 0 | 1 | -0.01 | See above
Benton | 4 | 0.97 | 0 | 1 | -0.03 | See below
Lincoln | 4 | 0.97 | 0 | 1 | -0.03 | See below
Linn | 4 | 0.97 | 0 | 1 | -0.03 | See below
Lane | 5 | 0.97 | 0 | 1 | -0.03 | Eugene, per NATIONAL BUILDING COST MANUAL 2023
Douglas | 6 | 0.97 | 0 | 0.98 | -0.01 | EXTRAPOLATED SAME AS ABOVE, ADJACENT COUNTY
Coos | 7 | 0.97 | 0 | 0.98 | -0.01 | EXTRAPOLATED SAME AS ABOVE, ADJACENT COUNTY
Curry | 7 | 0.97 | 0 | 0.98 | -0.01 | EXTRAPOLATED SAME AS ABOVE, ADJACENT COUNTY
Jackson | 8 | 0.96 | 0 | 0.98 | -0.02 | See below
Josephine | 8 | 0.96 | 0 | 0.98 | -0.02 | Grants pass, per NATIONAL BUILDING COST MANUAL 2023
Hood River | 9 | 1.03 | 0 | 1.05 | -0.02 | CARRIED SAME AS Clatsop/Columbia/Tillamook, same principle as previous entry
Sherman | 9 | 1.03 | 0 | 1.05 | -0.02 | See above
Wasco | 9 | 1.03 | 0 | 1.05 | -0.02 | See above
Crook | 10 | 1.03 | 0 | 0.98 | 0.05 | See below
Deschutes | 10 | 1.03 | 0 | 0.98 | 0.05 | Bend, per NATIONAL BUILDING COST MANUAL 2023
Jefferson | 10 | 1.03 | 0 | 0.95 | 0.08 | See above
Klamath | 11 | 0.92 | 0 | 0.95 | -0.03 | Klamath Falls, per NATIONAL BUILDING COST MANUAL 2023
Lake | 11 | 0.92 | 0 | 0.95 | -0.03 | See above
Gilliam | 12 | 0.97 | 0 | 0.97 | 0 | See above
Grant | 12 | 0.97 | 0 | 0.97 | 0 | See above
Morrow | 12 | 0.97 | 0 | 0.97 | 0 | See above
Umatilla | 12 | 0.97 | 0 | 0.97 | 0 | Pendleton, per NATIONAL BUILDING COST MANUAL 2023
Wheeler | 12 | 0.97 | 0 | 0.97 | 0 | See above
Baker | 13 | 0.92 | 0 | 0.99 | -0.07 | MEAN AVG SPLIT BETWEEN UMATILLA/MALHEUR
Union | 13 | 0.92 | 0 | 0.99 | -0.07 | See above
Wallowa | 13 | 0.92 | 0 | 0.99 | -0.07 | See above
Harney | 14 | 0.86 | 0 | 0.91 | -0.05 | See below
Malheur | 14 | 0.86 | 0 | 0.91 | -0.05 | Adrian, per NATIONAL BUILDING COST MANUAL 2023
|  | Selected Factor | 0
NOTES
Regions established by the State of Oregon BOLI Office
Relational rates between regions extrapolated from the National Building Cost Manual (2023)

## Escalation Calcs - READ ONLY
Escalation Calculator
Escalation Factor Summary |  |  |  | Historical Cost Indices | [5 empty] | Turner Construction Quarterly Index
Current Quarter: | 23-Q4 |  |  | Source |  |  | Instructions for Adding New Index Month |  |  | 18-Q1 | 1071
Escalation Indices for Estimate |  |  |  | FRED Graph Observations |  |  | 1. Search PPI code for latest observations. |  |  | 18-Q2 | 1089
Estimate Milestone | Date | Quarter | Factor | Federal Reserve Economic Data |  |  | 2. Log new observations at bottom of 'Index Data'. Copy down 'Quarter' Column formula, ensure observation is in same date format. |  |  | 18-Q3 | 1105
Original PCA Unit Rates | 2019-01-31 | 19-Q1 | 165.8333 | Link: https://fred.stlouisfed.org | [5 empty] | 18-Q4 | 1120
Replacement Budget Rates | 2023-03-01 | 23-Q1 | 229.2857 | Help: https://fredhelp.stlouisfed.org | [5 empty] | 19-Q1 | 1135 | 5.976%
Date of Estimate | 0/0/0000 | #VALUE! | #VALUE! | Economic Research Division | [5 empty] | 19-Q2 | 1149
Bond Date | 2024-11-05 | 24-Q4 | 249.9529 | Federal Reserve Bank of St. Louis |  |  | 3. Click into the 'Aggregated Quarterly Index Average' table (any field below the title). Go to the top toolbar and select 'Pivot Table' > Refresh > Refresh All. |  |  | 19-Q3 | 1162
Design Finish | 2025-11-05 | 25-Q4 | 262.6868 | PCU236222236222 | [5 empty] | 19-Q4 | 1177
Renovation Construction Start Date | 2025-11-05 | 25-Q4 | 262.6868 | Producer Price Index by Industry: New School Building Construction, Index Dec 2005=100, Monthly, Not Seasonally Adjusted | [5 empty] | 20-Q1 | 1189 | 4.758%
Renovation End Date | 2027-11-05 | 27-Q4 | 290.134 | [6 empty] | 20-Q2 | 1177
Renovation Midpoint | 2026-11-05 | 26-Q4 | 276.0695 | Index Data |  |  | Aggregated Quarterly Index Average |  | Q1 Yearly Changes | 20-Q3 | 1171
Replacement Construction Midpoint | 11/5/2026 | 26-Q4 | 276.0695 | Observation Date | PCU236222236222 | Quarter | Quarter | Average of PCU236222236222 |  | 20-Q4 | 1171
Escalation Factors |  |  |  | 2018-01-01 | 157.5 | 18-Q1 | 18-Q1 | 157.5 |  | 21-Q1 | 1172 | -1.43%
Legend |  |  |  | 2018-02-01 | 157.5 | 18-Q1 | 18-Q2 | 159.4 |  | 21-Q2 | 1187
Historical Index based on Bureau of labor Statistics PPI |  |  |  | 2018-03-01 | 157.5 | 18-Q1 | 18-Q3 | 160.1333 |  | 21-Q3 | 1207
Projected Index Based on Quarterly Escalation of: |  | 1.25% |  | 2018-04-01 | 159.4 | 18-Q2 | 18-Q4 | 164.4667 |  | 21-Q4 | 1230
Quarter | Escalation Factor |  | Historical Index | 2018-05-01 | 159.4 | 18-Q2 | 19-Q1 | 165.8333 | 5.291% | 22-Q1 | 1255 | 7.082%
18-Q1 | 157.5 |  | 157.5 | 2018-06-01 | 159.4 | 18-Q2 | 19-Q2 | 169.9667 |  | 22-Q2 | 1283
18-Q2 | 159.4 |  | 159.4 | 2018-07-01 | 160.1 | 18-Q3 | 19-Q3 | 171.3667 |  | 22-Q3 | 1311
18-Q3 | 160.1333 |  | 160.1333 | 2018-08-01 | 160.2 | 18-Q3 | 19-Q4 | 172.0667 |  | 22-Q4 | 1332
18-Q4 | 164.4667 |  | 164.4667 | 2018-09-01 | 160.1 | 18-Q3 | 20-Q1 | 173.3 | 4.503% | 23-Q1
19-Q1 | 165.8333 |  | 165.8333 | 2018-10-01 | 164.5 | 18-Q4 | 20-Q2 | 174.3667
19-Q2 | 169.9667 |  | 169.9667 | 2018-11-01 | 164.5 | 18-Q4 | 20-Q3 | 175.1
19-Q3 | 171.3667 |  | 171.3667 | 2018-12-01 | 164.4 | 18-Q4 | 20-Q4 | 174.1
19-Q4 | 172.0667 |  | 172.0667 | 2019-01-01 | 165.7 | 19-Q1 | 21-Q1 | 174.6333 | 0.7694%
20-Q1 | 173.3 |  | 173.3 | 2019-02-01 | 165.9 | 19-Q1 | 21-Q2 | 176.7333
20-Q2 | 174.3667 |  | 174.3667 | 2019-03-01 | 165.9 | 19-Q1 | 21-Q3 | 180.2927
20-Q3 | 175.1 |  | 175.1 | 2019-04-01 | 169.2 | 19-Q2 | 21-Q4 | 189.9913
20-Q4 | 174.1 |  | 174.1 | 2019-05-01 | 170.1 | 19-Q2 | 22-Q1 | 195.4427 | 11.92%
21-Q1 | 174.6333 |  | 174.6333 | 2019-06-01 | 170.6 | 19-Q2 | 22-Q2 | 204.341
21-Q2 | 176.7333 |  | 176.7333 | 2019-07-01 | 171.4 | 19-Q3 | 22-Q3 | 216.3233
21-Q3 | 180.2927 |  | 180.2927 | 2019-08-01 | 171.4 | 19-Q3 | 22-Q4 | 223.8403
21-Q4 | 189.9913 |  | 189.9913 | 2019-09-01 | 171.3 | 19-Q3 | 23-Q1 | 229.2857 | 17.32%
22-Q1 | 195.4427 |  | 195.4427 | 2019-10-01 | 172 | 19-Q4 | 23-Q2 | 232
22-Q2 | 204.341 |  | 204.341 | 2019-11-01 | 172.1 | 19-Q4 | (blank)
22-Q3 | 216.3233 |  | 216.3233 | 2019-12-01 | 172.1 | 19-Q4
22-Q4 | 223.8403 |  | 223.8403 | 2020-01-01 | 173.3 | 20-Q1
23-Q1 | 229.2857 |  | 229.2857 | 2020-02-01 | 173.4 | 20-Q1
23-Q2 | 232 |  | 232 | 2020-03-01 | 173.2 | 20-Q1
23-Q3 | 234.9 |  | #N/A | 2020-04-01 | 174.5 | 20-Q2
23-Q4 | 237.8362 |  | #N/A | 2020-05-01 | 174.4 | 20-Q2
24-Q1 | 240.8092 |  | #N/A | 2020-06-01 | 174.2 | 20-Q2
24-Q2 | 243.8193 |  | #N/A | 2020-07-01 | 175.2 | 20-Q3
24-Q3 | 246.8671 |  | #N/A | 2020-08-01 | 175.2 | 20-Q3
24-Q4 | 249.9529 |  | #N/A | 2020-09-01 | 174.9 | 20-Q3
25-Q1 | 253.0773 |  | #N/A | 2020-10-01 | 174 | 20-Q4
25-Q2 | 256.2408 |  | #N/A | 2020-11-01 | 174.2 | 20-Q4
25-Q3 | 259.4438 |  | #N/A | 2020-12-01 | 174.1 | 20-Q4
25-Q4 | 262.6868 |  | #N/A | 2021-01-01 | 174.4 | 21-Q1
26-Q1 | 265.9704 |  | #N/A | 2021-02-01 | 174.8 | 21-Q1
26-Q2 | 269.295 |  | #N/A | 2021-03-01 | 174.7 | 21-Q1
26-Q3 | 272.6612 |  | #N/A | 2021-04-01 | 176.4 | 21-Q2
26-Q4 | 276.0695 |  | #N/A | 2021-05-01 | 176.9 | 21-Q2
27-Q1 | 279.5204 |  | #N/A | 2021-06-01 | 176.9 | 21-Q2
27-Q2 | 283.0144 |  | #N/A | 2021-07-01 | 180.151 | 21-Q3
27-Q3 | 286.5521 |  | #N/A | 2021-08-01 | 180.279 | 21-Q3
27-Q4 | 290.134 |  | #N/A | 2021-09-01 | 180.448 | 21-Q3
28-Q1 | 293.7606 |  | #N/A | 2021-10-01 | 190.069 | 21-Q4
28-Q2 | 297.4326 |  | #N/A | 2021-11-01 | 190.208 | 21-Q4
28-Q3 | 301.1505 |  | #N/A | 2021-12-01 | 189.697 | 21-Q4
28-Q4 | 304.9149 |  | #N/A | 2022-01-01 | 194.963 | 22-Q1
29-Q1 | 308.7264 |  | #N/A | 2022-02-01 | 195.218 | 22-Q1
29-Q2 | 312.5854 |  | #N/A | 2022-03-01 | 196.147 | 22-Q1
29-Q3 | 316.4928 |  | #N/A | 2022-04-01 | 204.252 | 22-Q2
29-Q4 | 320.4489 |  | #N/A | 2022-05-01 | 204.212 | 22-Q2
30-Q1 | 324.4545 |  | #N/A | 2022-06-01 | 204.559 | 22-Q2
30-Q2 | 328.5102 |  | #N/A | 2022-07-01 | 215.917 | 22-Q3
30-Q3 | 332.6166 |  | #N/A | 2022-08-01 | 216.167 | 22-Q3
30-Q4 | 336.7743 |  | #N/A | 2022-09-01 | 216.886 | 22-Q3
|  |  |  | 2022-10-01 | 223.957 | 22-Q4
|  |  |  | 2022-11-01 | 223.939 | 22-Q4
|  |  |  | 2022-12-01 | 223.625 | 22-Q4
|  |  |  | 2023-01-01 | 226.857 | 23-Q1

## County Names (hidden)
Baker
Benton
Clackamas
Clatsop
Columbia
Coos
Crook
Curry
Deschutes
Douglas
Gilliam
Grant
Harney
Hood River
Jackson
Jefferson
Josephine
Klamath
Lake
Lane
Lincoln
Linn
Malheur
Marion
Morrow
Multnomah
Polk
Sherman
Tillamook
Umatilla
Union
Wallowa
Wasco
Washington
Wheeler
Yamhill

## District Names (hidden)
ID | District Name
2063 | Adel SD 21
2113 | Adrian SD 61
1899 | Alsea SD 7J
2252 | Amity SD 4J
2111 | Annex SD 29
2005 | Arlington SD 3
2115 | Arock SD 81
2041 | Ashland SD 5
2051 | Ashwood SD 8
1933 | Astoria SD 1
2208 | Athena-Weston SD 29RJ
1894 | Baker SD 5J
1969 | Bandon SD 54
2240 | Banks SD 13
2243 | Beaverton SD 48J
1976 | Bend-LaPine Administrative SD 1
2088 | Bethel SD 52
2095 | Blachly SD 90
2052 | Black Butte SD 41
1974 | Brookings-Harbor SD 17C
1896 | Burnt River SD 30J
2046 | Butte Falls SD 91
1995 | Camas Valley SD 21J
1929 | Canby SD 86
2139 | Cascade SD 5
2185 | Centennial SD 28J
1972 | Central Curry SD 1
2105 | Central Linn SD 552
2042 | Central Point SD 6
2191 | Central SD 13J
1902 | Clackamas ESD
1945 | Clatskanie SD 6J
1927 | Colton SD 53
2223 | Columbia Gorge ESD
2006 | Condon SD 25J
1965 | Coos Bay SD 9
1964 | Coquille SD 8
2186 | Corbett SD 39
1901 | Corvallis SD 509J
2216 | Cove SD 15
2086 | Creswell SD 40
1970 | Crook County SD
2089 | Crow-Applegate-Lorane SD 66
2050 | Culver SD 4
2190 | Dallas SD 2
2187 | David Douglas SD 40
2253 | Dayton SD 8
2011 | Dayville SD 16J
2017 | Diamond SD 7
2021 | Double O SD 28
1993 | Douglas County SD 15
1991 | Douglas County SD 4
1980 | Douglas ESD
2019 | Drewsey SD 13
2229 | Dufur SD 29
2043 | Eagle Point SD 9
2203 | Echo SD 5
2217 | Elgin SD 23
1998 | Elkton SD 34
2221 | Enterprise SD 21
1930 | Estacada SD 108
2082 | Eugene SD 4J
2193 | Falls City SD 57
2084 | Fern Ridge SD 28J
2241 | Forest Grove SD 15
2248 | Fossil SD 21J
2020 | Frenchglen SD 16
2245 | Gaston SD 511J
2137 | Gervais SD 1
1931 | Gladstone SD 115
2000 | Glendale SD 77
1992 | Glide SD 12
2007 | Grant ESD
2054 | Grants Pass SD 7
2100 | Greater Albany Public SD 8J
2183 | Gresham-Barlow SD 10J
2014 | Harney County SD 3
2015 | Harney County SD 4
2023 | Harney County Union High SD 1J
2013 | Harney ESD Region XVII
2114 | Harper SD 66
2099 | Harrisburg SD 7J
2201 | Helix SD 1
2206 | Hermiston SD 8
1975 | High Desert ESD
2239 | Hillsboro SD 1J
2024 | Hood River County SD
1895 | Huntington SD 16J
2215 | Imbler SD 11
2200 | InterMountain ESD
3997 | Ione SD R2
2053 | Jefferson County SD 509J
2049 | Jefferson ESD
2140 | Jefferson SD 14J
1934 | Jewell SD 8
2008 | John Day SD 3
2107 | Jordan Valley SD 3
2219 | Joseph SD 6
2091 | Junction City SD 69
2109 | Juntura SD 12
2057 | Klamath County SD
2056 | Klamath Falls City Schools
2262 | Knappa SD 4
2212 | La Grande SD 1
2059 | Lake County SD 7
2058 | Lake ESD
1923 | Lake Oswego SD 7J
2064 | Lane ESD
2101 | Lebanon Community SD 9
2097 | Lincoln County SD
2098 | Linn Benton Lincoln ESD
2012 | Long Creek SD 17
2092 | Lowell SD 71
2112 | Malheur County SD 51
2106 | Malheur ESD Region 14
2085 | Mapleton SD 32
2094 | Marcola SD 79J
2090 | McKenzie SD 68
2256 | McMinnville SD 40
2048 | Medford SD 549C
2205 | Milton-Freewater Unified SD 7
2249 | Mitchell SD 55
1925 | Molalla River SD 35
1898 | Monroe SD 1J
2010 | Monument SD 8
2147 | Morrow SD 1
2145 | Mt Angel SD 91
2148 | Multnomah ESD
1968 | Myrtle Point SD 41
2198 | Neah-Kah-Nie SD 56
2199 | Nestucca Valley SD 101
2254 | Newberg SD 29J
1966 | North Bend SD 13
2004 | North Central ESD
1924 | North Clackamas SD 12
1996 | North Douglas SD 22
2061 | North Lake SD 14
2141 | North Marion SD 15
2214 | North Powder SD 8J
2143 | North Santiam SD 29J
4131 | North Wasco County SD 21
2230 | Northwest Regional ESD
2110 | Nyssa SD 26
1990 | Oakland SD 1
2093 | Oakridge SD 76
2108 | Ontario SD 8C
1928 | Oregon City SD 62
1926 | Oregon Trail SD 46
2060 | Paisley SD 11
2181 | Parkrose SD 3
2207 | Pendleton SD 16
2192 | Perrydale SD 21
1900 | Philomath SD 17J
2039 | Phoenix-Talent SD 4
2202 | Pilot Rock SD 2
2016 | Pine Creek SD 5
1897 | Pine Eagle SD 61
2047 | Pinehurst SD 94
2081 | Pleasant Hill SD 1
2062 | Plush SD 18
1973 | Port Orford-Langlois SD 2CJ
2180 | Portland SD 1J
1967 | Powers SD 31
2009 | Prairie City SD 4
2045 | Prospect SD 59
1946 | Rainier SD 13
1977 | Redmond SD 2J
2001 | Reedsport SD 105
2218 | Region 18 ESD
2182 | Reynolds SD 7
1999 | Riddle SD 70
2188 | Riverdale SD 51J
2044 | Rogue River SD 35
2142 | Salem-Keizer SD 24J
2104 | Santiam Canyon SD 129J
1944 | Scappoose SD 1J
2103 | Scio SD 95
1935 | Seaside SD 10
2257 | Sheridan SD 48J
2195 | Sherman County SD
2244 | Sherwood SD 88J
2138 | Silver Falls SD 4J
1978 | Sisters SD 6
2096 | Siuslaw SD 97J
1949 | South Coast ESD
2022 | South Harney SD 33
2087 | South Lane SD 45J3
1994 | South Umpqua SD 19
2225 | South Wasco County SD 1
2025 | Southern Oregon ESD
2247 | Spray SD 1
2083 | Springfield SD 19
1948 | St Helens SD 502
2144 | St Paul SD 45
2209 | Stanfield SD 61
2018 | Suntex SD 10
2003 | Sutherlin SD 130
2102 | Sweet Home SD 55
2055 | Three Rivers/Josephine County SD
2242 | Tigard-Tualatin SD 23J
2197 | Tillamook SD 9
2222 | Troy SD 54
2210 | Ukiah SD 80R
2204 | Umatilla SD 6R
2213 | Union SD 5
2116 | Vale SD 84
1947 | Vernonia SD 47J
2220 | Wallowa SD 12
1936 | Warrenton-Hammond SD 30
1922 | West Linn-Wilsonville SD 3J
2117 | Willamette ESD
2255 | Willamina SD 30J
2002 | Winston-Dillard SD 116
2146 | Woodburn SD 103
2251 | Yamhill Carlton SD 1
1997 | Yoncalla SD 32