SP00989  (Special Provisions for the 2021 Book) 	(Bidding on or after: 02-01-21

Last updated: 02-17-21)

# SECTION 00989 - PHOTOVOLTAIC EQUIPMENT INSTALLATION

(Follow all instructions and make all edits with “Track Changes” turned on. This Section is not published in the Oregon Standard. If there are no instructions [orange text] above a subsection, paragraph, sentence, or bullet, then include it in the project, unless the item(s) that are included in the subsection, paragraph, sentence, or bullet are not required on the Project and then they should be deleted. In general do not re-number or re-letter subsections when item(s) are deleted. Delete all orange text before preparing the final document.

The Work covered under this Section is diverse and this boilerplate may not include Specifications for all the Work or ITS elements on the Project. Modify as necessary by adding, deleting, or revising language for the specific project requirements. Modifications to this Section, other than deleting language not required, will require ODOT Technical Resource and State Specifications Engineer approval.)

Section 00989, which is not a Standard Specification, is included in this Project by Special Provision.

## Description

(In the following subsection .00, delete the language in orange parentheses that does not apply and delete the orange parentheses.)

00989.00  Scope - In addition to requirements of Section (00960,) (and) (00985) install ITS photovoltaic systems as shown or specified.

00989.01  Regulations, Standards, and Codes - Comply with the following standards where applicable:

Underwriters Laboratories (UL)

50-2015 - Enclosures for Electrical Equipment, Non-Environmental Considerations

83-2017 - Thermoplastic-Insulated Wires and Cables

498-2016 – Molded-Case Circuit Breakers, Molded-Case Switches, and Circuit-Breaker Enclosures

508-2018 – Standard for Industrial Control Equipment

508A-2018 - Standard for Industrial Control Panels

1059-2001 – Standard for terminal

1561-2011 - Standard for Dry-Type General Purpose and Power Transformers

1581-2001 - Reference Standard for Electrical Wires, Cables, and Flexible Cords

1685-2015 - Standard for Vertical-Tray Fire-Propagation and Smoke-Release Test for Electrical and Optical-Fiber Cables

1703-2002 - Standard for Flat-Plate Photovoltaic Modules and Panels

1741-2010 - Standard for Inverters, Converters, Controllers and Interconnection System Equipment for Use With Distributed Energy Resources

(In the following subsection .02, delete the language that does not apply.)

00989.02  Submittals - Submit according to 00150.37, within 30 Calendar Days after execution of the Contract, the following:

Photovoltaic Modules according to 00989.10

Module Mounting Bracket according to 00989.11

Photovoltaic Module Combiner Cabinet according to 00989.12

DC Disconnect according to 00989.13

DC Circuit Breakers according to 00989.14

Photovoltaic Charge Controller according to 00989.15

DC Load Controller according to 00989.16

Batteries according to 00989.17

Battery Enclosure according to 00989.18

Controller cabinet according to 00989.19

Include the manufacturer’s name, model numbers, catalog sheets and other descriptive literature of proposed materials. Provide the catalog sheets and literature including technical data, physical properties and operational description in sufficient detail to demonstrate the equipment meets these specifications.

## Materials

(Use the following subsection .10 when photovoltaic modules are required. Fill in the appropriate blanks.)

00989.10  Photovoltaic Modules - Furnish photovoltaic modules with cables that meet the following requirements:

| Module Characteristic Table |  |
| --- | --- |
| Maximum Power: | __ Watts or greater |
| Maximum Voltage: | __ Volts or greater |
| Maximum Power Point Current: | __ Amps or greater |
| Open Circuit Voltage: | __ Volts or less |
| Short Circuit Current: | __ Amps or less |
| Maximum System Voltage: | __ V |
| Length: | __ inches maximum |
| Width: | __ inches maximum |
| Weight: | __ lbs. maximum |
| Wind Load Rating: | __ mph minimum |

Furnish photovoltaic modules with a minimum combined total of ___ watts at rated maximum power that are UL 1703 listed and be constructed using an anodized aluminum or similar frame.

(Use the following subsection .11 when module mounting brackets are required. Fill in the appropriate blanks.)

00989.11  Module Mounting Bracket - Furnish mounting hardware to mount the photovoltaic modules on the side-of-pole. Furnish bracket sized to fit the modules selected and mount to the metal pole selected. Mount the modules as ____ arrays, with ____ panels on the first array, and ____ panels on the second array. Furnish stainless steel nuts, bolts, washers, and band clamps. The mounting assembly is to be rated for wind loads up to 120 mph and be constructed from anodized aluminum, powder coated aluminum, 304 stainless steel, or 316 stainless steel.

(Use the following subsection .12 when Photovoltaic module combiner cabinet is required.)

00989.12  Photovoltaic Module Combiner Cabinet - Furnish NEMA Type 3R rated, UL 1741 listed enclosures with terminals to combine the photovoltaic modules into one circuit. Protect each photovoltaic module input circuit with an overcurrent protection device sized as shown. Furnish cabinet constructed from anodized aluminum, powder coated aluminum, 304 stainless steel, or 316 stainless steel.

(Use the following subsection .13, when DC disconnects are required.)

00989.13  DC Disconnect - Furnish DC Disconnect that is UL 508 listed for overcurrent protection and has a means for disconnecting the photovoltaic and battery system’s circuits. Include DC circuit breakers for protecting the photovoltaic, battery, and load distribution circuits, circuit breaker sizing as shown. Provide a DC bonding block for grounding.

(Use the following subsection .14, when DC circuit breakers are required.)

00989.14  DC Circuit Breakers - Furnish DC circuit breakers rated for 150V DC minimum, UL 489 listed, and DIN rail mounted. Size circuit breakers and label as shown.

(Use the following subsection .15, when photovoltaic charge controllers are required. Fill in the appropriate blanks.)

00989.15  Photovoltaic Charge Controller - Furnish a photovoltaic charge controller that meets the following requirements:

| Charge Controller Characteristic Table |  |
| --- | --- |
| Controller Charge Type | Maximum Power Point Tracking |
| Voltage Step Down Capability | Convert photovoltaic module voltage selected to 12 VDC nominal for battery charging |
| Maximum Output Current: | __A DC continuous |
| Charging Regulation | 4 stages minimum |
| Short Circuit Protection: | Electronic with auto-reset |
| LCD Meter Module: | Photovoltaic Input Voltage |
|  | Photovoltaic Input Current |
|  | Battery Voltage |
|  | Battery Charging Current |
|  | Cumulative amp/watt hours |
| Operating Temperature Range: | -__ to __ degrees F |
| Mounting: | Module/Wall |
| Wire Size: | Capable of accepting _ AWG conductors |
| Accepted Battery Type: | Sealed AGM |
| Temperature Compensation: | Provide an external battery temperature sensor to the charge control set points. |
| Listing | UL 1741 |

(Use the following subsection .16, when DC load controller is required. Fill in the appropriate blanks.)

00989.16  DC Load Controller - Furnish a DC load controller that meets the following requirements:

| Load Controller Characteristic Table |  |
| --- | --- |
| Controller Charge Type | Pulse Width Modulation |
| Voltage Configuration: | 12V DC |
| Minimum Charging/Load Current: | __A DC continuous |
| Charge Regulation: | Solid State |
| Short Circuit Protection: | Electronic with auto-reset |
| LCD Meter Module: | Battery Voltage |
|  | Load Current |
|  | Cumulative amp/watt hours |
| Temperature Range: | -40 to 113 degrees F |
| Mounting: | Module/Wall |
| Wire Size: | Capable of accepting __ AWG conductors |
| Load Control: | Low voltage disconnect and reconnect |
| Listing | UL 1741 |

(Use the following subsection .17, when batteries are required. Fill in the appropriate blanks.)

00989.17  Batteries - Furnish a system of batteries that meets the following requirements:

| Battery Characteristic Table |  |
| --- | --- |
| Voltage: | 6V DC or 12V DC, 6V DC batteries may be used to form a 12V DC base system. |
| Type: | Absorbed glass mat (AGM) sealed deep cycle lead acid |
| 24 Hour Rate: | ___ amp-hours minimum |
| Designed Maintenance Life: | _ years |
| Length: | _ inches maximum |
| Width: | _ inches maximum |
| Height: | _ inches maximum |
| Weight: | _ lbs. maximum |

Furnish a minimum of ____ amp-hours at rated capacity. This includes ____ Days autonomy factoring in temperature de-rating and discharge limit. Include all clamps, connectors, wiring, and other Incidental Materials as needed to wire and secure batteries.

(Use the following subsection .18, when battery enclosures are required.)

00989.18  Battery Enclosure - Furnish a battery enclosure that is UL 50 listed, Type 3R (ventilated), and be constructed from anodized aluminum, powder coated aluminum, 304 stainless steel, or 316 stainless steel. Place vents near the top of the enclosure to prevent the buildup of gases. Size enclosure to fit all of the batteries required for the system plus 2 additional batteries of the same size for future expansion. Include a 2 or 3 point locking mechanism with an integrated interchangeable lock core.

Furnish racks or trays that are rigid metal, designed to support the load, treated to be resistant to deteriorating action by the electrolyte, and included with non-conducting members directly supporting the cells.

The battery trays are frames of nonconductive material and constructed or treated so as to be resistant to deteriorating action by the electrolyte.

Furnish battery enclosure that is ground mounted.

(Use the following subsection .19, when controller cabinets are required.)

00989.19  Controller Cabinet - Furnish enclosure constructed from 14 gauge Type 304 or 316 stainless steel, UL 50 listed, Type 3R ventilated, and with a #4 brushed finish. Remove all sharp edges. Include door with continuous hinge, seamless gasket that is liquid-tight, and padlockable. Enclosure dimensions are location specific and shown on plans.

## Construction

00989.40  Installation - Install the Equipment as specified, shown, and according to the manufacturer’s instructions. Ground the Photovoltaic Power System according to Article 690 of NFPA 70, the National Electrical Code.

00989.41  Photovoltaic Component Identification and Marking - Photovoltaic modules, module combiner, DC disconnect, circuit breakers, charge controller, load controller, batteries, battery enclosure, and wiring are to be marked according to Article 690 of NFPA 70, the National Electrical Code.

## Measurement

00989.80  Measurement - No measurement of quantities will be made for Work performed under this Section.

## Payment

(Use one of the following two options for subsection .90)

[Option 1. Use this subsection .90 if site work needs to be broken out by Pay Items]

00989.90  Payment - The accepted quantities of Work performed under this Section will be paid for at the Contract unit price, per unit of measurement, for the following items:

(Add additional pay item(s) as required for the Schedule of Items.)

Pay Item		Unit of Measurement

(a)	Photovoltaic Equipment Installation, Site _____	Lump Sum

(b)	Photovoltaic Equipment Installation, Site _____	Lump Sum

Payment will be payment in full for furnishing and placing all Materials, labor, and Incidentals necessary to complete the Work as specified.

No separate or additional payment will be made for:

required submittals and documentation

assistance for commissioning Equipment and systems

[End Option 1]

[Option 2. Use this subsection .90 if site work does NOT need to be broken out per site.)

00985.90  Payment - The accepted quantities of Work performed under this Section will be paid for at the Contract lump sum amount for the item “Photovoltaic Equipment Installation".

Payment will be payment in full for furnishing and placing all Materials, labor, and Incidentals necessary to complete the Work as specified.

No separate or additional payment will be made for:

required submittals and documentation

assistance for commissioning Equipment and systems

[End Option 2]