SP02475  (Special Provisions for the 2024 Book) 	(Bidding on or after: 12-01-25

Last updated: 08-28-25)

# SECTION 02475 – POTABLE WATER FITTING MATERIALS

(Follow all instructions and make all edits with “Track Changes” turned on. If there are no instructions [purple text] above a subsection, paragraph, sentence, or bullet, then include it in the Project. Delete all purple text before preparing the final document. All other modifications to this Section will require ODOT Technical Resource and State Specifications Engineer approval.)

Comply with Section 02475 of the Standard Specifications modified as follows:

02475.20  Ductile Iron Pipe Fittings - Replace this subsection, except for the subsection number and title, with the following:

Fittings for ductile iron pipe shall meet the requirements of AWWA C110 or AWWA C153, and shall have a minimum working pressure rating of 250 psi. Joints shall meet the requirements of AWWA C111. Fittings shall be cement mortar lined and seal coated, meeting the requirements of AWWA C104. Provide gaskets for ductile iron flanged joints that are composed of synthetic rubber, full faced, 1/8-inch thick, and conform to ANSI/AWWA C111/A21.11. Ring gaskets will be permitted only where specified or shown. The type, material and identification mark for bolts and nuts shall be provided.