| Table 1. | Alarm Set Point Verification (example regulatory limits and optimization goals for conventional filtration are shown) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Alarm | Intended Purpose |  | Set Points |  |  |  | Verified in SCADA or in meter controller | Tested Alarm & Auto Dialer |
|  | Compliance | Optimization | Autodial |  | Shutdown |  |  |  |
|  | Applicable Regulatory Limit | Applicable Optimization Goal | Autodial Set Point & Phone # |  | Auto-Shutdown Set Point |  |  |  |
| IFE NTU High N/A | 1 NTU N/A | 0.10 NTU N/A | ___ NTU (___) ___-_____ N/A |  | ___ NTU N/A |  |  |  |
| IFE NTU High-High N/A | 2 NTU N/A | 0.30 NTU N/A | ____NTU (___) ___-_____ N/A |  | ___ NTU N/A |  |  |  |
| CFE NTU High N/A | 0.3 NTU N/A | 0.10 NTU N/A | ___ NTU (___) ___-_____ N/A |  | ___ NTU N/A |  |  |  |
| CFE NTU High-High N/A | 1 NTU N/A | 0.30 NTU N/A | ___ NTU (___) ___-_____ N/A |  | ___ NTU N/A |  |  |  |
| EP Chlorine Low N/A | 0.2 mg/l - High enough to meet required CT - High enough for detectable residual throughout distribution system N/A | 0.2 mg/l - High enough to meet required CT - High enough to maintain 0.2 mg/l throughout distribution system N/A | ___ mg/l (___) ___-_____ High enough to meet required CT High enough for detectable residual throughout distribution system N/A |  | ___ mg/l High enough to meet required CT High enough to maintain 0.2 mg/l throughout distribution system N/A |  |  |  |
| EP Chorine High N/A | 4.0 mg/l N/A | 2.5 mg/l N/A | ___ mg/l (___) ___-_____ N/A |  | ___ mg/l N/A |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |
| Sign: |  |  |  | Date: |  |  |  |  |
| N/A = Not applicable for intended purpose or not available for alarm and set points NTU = Nephelometric turbidity units IFE = Individual filter effluent CFE= Combined filter effluent EP = Entry point to the distribution system (after all treatment and prior to or at first customer) CT = (chlorine Concentration in mg/l) x (contact Time in minutes) |  |  |  |  |  |  |  |  |
| Oregon Health Authority – Public Health Division - Center for Health Protection – Drinking Water Services |  |  |  |  |  |  |  |  |