## Instructions
Instructions for Using the Existing Stage 1 Data Organizing Worksheet to Select Stage 2 Monitoring Locations
The following are step-by-step instructions on how to use the Existing Stage 1 Data Organizing Worksheet located on the tabs below. Note that you are not required to use this worksheet, it is simply provided to help you organize your monitoring results.
STEP #1 | Enter location of the sampling sites, including:
• All Stage 1 DBP sampling sites
• Any additional TTHM or HAA5 locations sampled
STEP #2 | Enter the most recent monitoring results for each location.
• If you monitor quarterly, enter the last 4 quarters of results for each location.
• If you monitor yearly, enter the last result for each location(s) only. You will be looking at just one data point.
• If you have older data, you may also want to look at years with high TTHM and HAA5 levels (which often occur during warm weather or periods with high TOC) on another copy of this worksheet.
• Do not look at data collected earlier than the last treatment/distribution change.
STEP #3 | Calculate the LRAA for each sampling site.
• If you monitor quarterly, the LRAA is the average of the last 4 quarters. LRAA = Q1+Q2+Q3+Q4/4
• If you monitor yearly, the LRAA is simply your last sample result.
STEP #4 | Select Stage 2 Compliance Monitoring Sites.
• Select the location with the highest TTHM LRAA as your High TTHM site.
• Select the location with the highest HAA5 LRAA as your High HAA5 site. If your highest TTHM and HAA5 occur at the same site, choose your second highest HAA5 LRAA as your High HAA5 site.
• Continue selecting sites by alternating between locations with high TTHMs and high HAA5s until the required number of Stage 2 compliance monitoring locations have been identified. If a site has already been selected, pick the next highest available site.
• Surface water & GWUDI systems serving ≤3,300 and groundwater systems <500 can take a dual sample set at one location if highest TTHM and HAA5 LRAAs occur at the same site (otherwise take one sample at two separate locations for High TTHM and High HAA5).

## Blank Worksheet
Existing Stage 1 Data - TTHM
Sampling Site | Quarter 1 | Quarter 2 | Quarter 3 | Quarter 4 | LRAA | Site Selection
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Existing Stage 1 Data - HAA5
Sampling Site | Quarter 1 | Quarter 2 | Quarter 3 | Quarter 4 | LRAA | Site Selection
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!

## Example
Existing Stage 1 Data - TTHM
Sampling Site | Quarter 1 | Quarter 2 | Quarter 3 | Quarter 4 | LRAA | Site Selection
Stage 1 - 1 | 0.048 | 0.054 | 0.087 | 0.063 | 0.063 | 2nd highest THM
Stage 1 - 2 | 0.068 | 0.081 | 0.09 | 0.074 | 0.07825 | High TTHM Site
Stage 1 - 3 | 0.036 | 0.068 | 0.065 | 0.055 | 0.056 | -
Stage 1 - 4 | 0.042 | 0.06 | 0.058 | 0.047 | 0.05175 | -
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Existing Stage 1 Data - HAA5
Sampling Site | Quarter 1 | Quarter 2 | Quarter 3 | Quarter 4 | LRAA | Site Selection
Stage 1 - 1 | 0.024 | 0.024 | 0.035 | 0.045 | 0.032 | -
Stage 1 - 2 | 0.012 | 0.035 | 0.032 | 0.034 | 0.02825 | -
Stage 1 - 3 | 0.035 | 0.046 | 0.061 | 0.054 | 0.049 | High HAA5 Site
Stage 1 - 4 | 0.034 | 0.044 | 0.059 | 0.054 | 0.04775 | 2nd highest HAA5
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!
0 |  |  |  |  | #DIV/0!