## Calculation
Basics for Small Water Systems in Oregon:
Storage Tank Chlorination |  |  |  |  | Options for Disinfection by Chlorination:
Disinfection concentrations and times are based on AWWA Standard C652 for storage tanks cited in: OAR 333-061-0050 "Construction Standards" (10)(d) dated 19 Apr 2010, page 297 |  |  |  |  | Method A. Filling the tank or reservoir with a 10 mg/L chlorine solution and allowing it to remain for 6a or 24 hours (see Table).
Method B. Filling the reservoir with a 50 mg/L chlorine solution and allowing it to stand for 6 hours (see Table).
| Question: How much chlorine is added to a tank? |  |  |  | Method C. Spraying or brushing on a 200 mg/L chlorine solution and allowing it to remain for 3 hours (calculation not provided).
Volume to be disinfected = |  |  |  | 500 | gallons
(input tank volume above in yellow shaded cell)
Chlorination Dose for Storage Tank of Volume Specified Above |  | Method Ab | Method Bc | Units
Chlorine Concentration |  | 10 | 50 | mg/L | (Chlorine Concentration values [yellow, or grey, cells]
Method Exposure Time |  | 6a or 24 | 6 | hours | can be changed for custom calculations)
Chlorine Source Material…
Bleach 5% Solution |  | 0.1 | 0.5 | gallonsd | E Note that to achieve Method concentration
Bleach 8.25% Solution |  | 0.060606 | 0.30303 | gallonsd | add more chlorine than specified here.
Bleach 12.5% Solution |  | 0.04 | 0.2 | gallons | Important: Measure chlorine concentration to confirm Method's target concentration. Test strips used in restaurant inspection (for detecting higher chlorine levels) may be useful, or dilute a sample to your test kit range
Dry Chlorine (65% by wt) |  | 0.064614 | 0.32307 | pounds
|  | 0.029309 | 0.14654 | kilograms
a Six (6) hours for addition by continuous feed during tank filling.
b For Pipes, Method A using 24 hours is applicable (shorter time at higher dose may be allowed, see Guidance).
c For Wells, Method B using 24 hours is applicable (shorter time at higher dose may be allowed, see Guidance).
d Gallons to Cups conversion: |  | Gallons | Cups |  | Weight of dry chlorine with a lower percentage than 65% can be calculated by
| (gal x 16 = cups) | 1.6 | 25.6 |  | dividing 65% by the product's % chlorine (e.g., 65%/47%) times result in table.

## DATA
DATA FOR SLOPE CALCULATIONS
(Data from FACT SHEET 3.7 in UNIT 3 - Operations of Staff Training Reference)
Reservoir (Gal) | Gallons 5% Bleach |  |  | Reservoir (Gal) | Pounds 65% Dry Chlorine
1000 | 0.5 |  |  | 10000 | 3.5
2000 | 1 |  |  | 20000 | 6.5
3000 | 1.5 |  |  | 30000 | 10
4000 | 2 |  |  | 40000 | 13
5000 | 2.5 |  |  | 50000 | 16
10000 | 5 |  |  | 100000 | 32
20000 | 10 |  |  | 200000 | 64
30000 | 15 |  |  | 300000 | 100
40000 | 20 |  |  | 400000 | 130
50000 | 25 |  |  | 500000 | 160
Slope 5% Sol = | 0.0005 | gal/gal | Slope Dry Wt = |  | 0.00032307 | lb/gal | Conversion factors
[7 empty] | 2.2046 | lb/kg
[7 empty] | 3.7854 | L/gal
Reference Concentration | 2.5e-05 | mg/L |  |  | 2.5163e-05 | mg/L
25 | mg/L reference concentration (from tables in training manual)