Oregon School for the Deaf

# Facilities Assessment Update 2024

# Acknowledgments

BRIC Architecture, Inc is pleased to submit this update to the Oregon School for the Deaf’s existing facility assessment report. These findings and recommendations are a product of our high-level visual assessments of building conditions completed in December 2023 and support the development of a Long-Range Facility Plan to be developed in early 2024.

OREGON DEPARTMENT OF EDUCATION

Melissa Garner, M. Ed. Director of Business Services

Philip Hofmann Deputy Director of Procurement

OREGON SCHOOL FOR THE DEAF

Brian Marshall Maintenance Supervisor

Maintenance Team

BRIC ARCHITECTURE, INC.

David Johnson, AIA Principal-in-Charge

Nancy Rad, AIA NCIDQ Senior Associate

Beth Cantrell, AIA

STEVE SMITH PHOTOGRAPHY

Drone Photographer

# Purpose

## BACKGROUND

The Oregon School for the Deaf (OSD) has been in existence since 1870 and at its current location at 999 Locust Street NE, Salem, Oregon 97301 since 1910. The campus includes 19 buildings of various ages, styles, materials, sizes, and uses totaling 270,000 sf.

The campus is nestled amongst residential neighborhoods and commercial development. A railroad line defines the southeast border. The 37.3-acre campus is covered with large trees, lawns, and paths that connect the buildings and athletic fields. The campus serves the needs of both residential and day students during the academic school year. Special programs are run on campus year-round.

OSD is the only public school for Deaf in Oregon to provide specially designed instruction to students in kindergarten through age 21, from 49 different school districts from all areas of the state.

On-campus opportunities are provided at OSD for individual students to experience not only deaf education, but cultural and social engagement essential to developing communication and interaction abilities. While the OSD campus continues to serve the needs of the Deaf community, this report identifies a range of improvements needed to maintain and develop those services.

The OSD campus celebrates its over 110 years of existence in this location. The majority of campus buildings were constructed between 1958 and 1975. The condition of the overall campus facilities demonstrates the deficiencies of aging buildings and site infrastructure. Buildings of this vintage have inherent issues to be addressed in order to meet today’s needs and expectations. This report recognizes those needs and ranks those needs by priority.

# Process

This report is based on previous studies and reports, updating information to reflect conditions observed in December 2023. Assessments of architectural, site, structural, plumbing, mechanical, electrical, and technology systems are based on high-level, architect-led, visual assessments of building conditions. Additionally, this report includes known conditions-related deficiencies flagged by Oregon School for the Deaf maintenance and facility personnel.

References used as a base to complete the matrix include:

| Title | Year | Source |
| --- | --- | --- |
| OTAK Facilities Study | 2008 | OSD |
| State Legislature Budget Report | 2011 | Public Records |
| Area Plan for School for Deaf | 2018 | OSD |
| Site Systems Tier 2 FCA Analysis | 2018 | OSD |
| Tree of Life (Hazardous Material Survey) | 2023 | OSD |

Our architect-led assessment team spent two full working days on site conducting high-level visual assessments of building conditions. The teams were accompanied by OSD maintenance staff as they reviewed each building. Information provided by OSD staff was essential. Findings from the site visits were recorded into the Uniformat II Level 3 Matrix to describe and update noted deficiencies per line item for the campus/site and each building.

In order to aid in reviewing the large number of issues and conditions-related deficiencies our team observed, we categorized conditions as follows:

## SAFETY

Conditions and issues related to the physical safety of students, staff, and other potential users of campus facilities.

## FIRE LIFE SAFETY/CODE

Antiquated infrastructure and other deficiencies related to current applicable building and fire code requirements and standards.

## SECURITY

Observed issues related to the safety and security of students, staff, and of physical property.

## ACCESSIBILITY

Deficiencies and other issues related to accessibility standards including the Americans with Disabilities Act (ADA).

## HAZARDOUS MATERIALS

The presence of known hazardous building materials including (but not limited to) asbestos, lead, and mercury.

## INDOOR AIR QUALITY AND VENTILATION

Indoor Air Quality refers to the air quality within and around buildings and structures, especially as it relates to the health and comfort of building occupants.

## ENERGY

Deficiencies related to current State of Oregon energy code requirements for the performance of insulation, equipment, windows, lighting, and other building elements.

## GENERAL MAINTENANCE

Necessary minor repairs or maintenance that can be performed by OSD maintenance staff.

## DEFERRED MAINTENANCE

Significant repairs, construction, or other improvements that will likely require work by a licensed qualified contractor.

## SCOPE OF WORK

Descriptions of recommended actions associated with each identified issue or deficiency.

## ROUGH ORDER OF MAGNITUDE COSTS

Rough Order of Magnitude (ROM) costs are generated per line item in response to the scope of work for budgeting purposes. Each ROM cost line item includes design

contingency and general contractor fees.

## EXCLUSIONS AND ASSUMPTIONS

Data/Telecom, access control and lock down systems require further discussion to better understand what is needed.

Landscape, furniture, fixtures and equipment were not included in the base information provided.

Campus wide LED lamp replacements in existing light fixtures, fire alarm upgrades and adding security cameras are work in progress or on the schedule unless noted otherwise. Clock system is understood to be working well.

Soft costs for further investigations & testing needed for seismic, hazardous materials and emergency power.

Existing steam tunnel system was not accessed by the assessment team.

# Understanding Needs

The OSD campus is comprised of 19 buildings with a variety of uses and a range of physical conditions. This report is intended to prioritize observed issues and deficiencies.

## Buildings By Use

### Residential

| BUILDING | CURRENT USE |
| --- | --- |
| 03 Peterson Hall | Girls Dormitory |
| 05 Lindstrom Hall | Boys Dormitory |
| 17 New Dormitory | Student Recreation and Rented to the Public |

### Educational

| BUILDING | CURRENT USE |
| --- | --- |
| 02 Wallace Hall | Adult Education |
| 04 Kuenzi Hall | Elementary School & Museum |
| 09 Hokanson Gym | Physical Education & STEAM |
| 11 Peck Gym | Gymnasium & Pool |
| 12 Ulmer Building | High School |
| 13 Smith Hall | Elementary & Middle School |

### Student Support

| BUILDING | CURRENT USE |
| --- | --- |
| 07 Clatterbuck Building | Dining Hall & Infirmary |

### Facilities Support

| BUILDING | CURRENT USE |
| --- | --- |
| 08 Maintenance/Central Plant | Facilities support |
| 10 Paint Shop | Facilities support |

### Vacant

| BUILDING | CURRENT USE |
| --- | --- |
| 01 Carpenter House & 14 Garage | None |
| 06 Tillinghast Hall & 16 Carport | None |

## FACILITY CONDITIONS INDEX

Facility Conditions Index is used as a benchmark to compare the relative condition of a group of facilities.

Facility Conditions Index s obtained by aggregating the total cost of any needed or outstanding repairs, renewal or upgrade requirements at a building compared to the current replacement value of the building components. It is the ratio of the “repair needs” to replacement value” expressed in percentage terms.

A higher Facility Conditions Index may indicate the need for major repairs or improvements, while a low score means the facility is well-maintained and in good shape. FCI plays a crucial role in maintaining the functionality and safety of a facility and helps in making informed decisions about upkeep, upgrades, and capital improvement.

Facility Conditions Index is ranked as follows:

- Less than 10 percent equals excellent

- 11 to 20 percent equals good

- 21 to 40 percent equals’ fair

- 41 to 60 percent equals poor

- More than 60 percent equals deficient

### Residential

| Facility Number and Name | REPLACEMENT COST |  | FCI | TOTAL ASSESSED NEEDS |
| --- | --- | --- | --- | --- |
| 03 Peterson Hall |  | $12,727,085 | 47% | $5,921,306 |
| 05 Lindstrom Hall |  | $17,522,450 | 54% | $14,964,024 |
| 17 New Dorm |  | $1,834,853 | 12% | $220,782 |

### Educational

| Facility Number and Name | REPLACEMENT COST | FCI | TOTAL ASSESSED NEEDS |
| --- | --- | --- | --- |
| 02 Wallace Hall | $3,350,970 | 61% | $2,056,643 |
| 04 Kuenzi | $16,879,752 | 50% | $8,477,072 |
| 09 Hokanson Gym | $5,773,680 | 63% | $3,648,291 |
| 11 Peck Gym | $12,941,208 | 16% | $2,062,454 |
| 12 Ulmer | $9,608,625 | 54% | $5,157,464 |
| 13 Smith Hall | $22,538,736 | 13% | $2,925,251 |

### Student Support

| Facility Number and Name | REPLACEMENT COST | FCI | TOTAL ASSESSED NEEDS |
| --- | --- | --- | --- |
| 07 Clatterbuck | $18,520,488 | 24% | $4,508.557 |

### Facilities Support

| Facility Number and Name | REPLACEMENT COST |  | FCI | TOTAL ASSESSED NEEDS |
| --- | --- | --- | --- | --- |
| 08 Central Plant |  | $8,959,950 | 29% | $2,596,014 |

### Vacant

| Facility Number and Name | REPLACEMENT COST | FCI | TOTAL ASSESSED NEEDS |
| --- | --- | --- | --- |
| 01 Carpenter House & 14 Garage | $469,476 | 128% | $602,159 |
| 06 Tillinghast & 16 Carport | $1,143,180 | 98% | $1,120,355 |

### Campus Totals

| REPLACEMENT COST | TOTAL ASSESSED NEEDS |
| --- | --- |
| $142,570,153 | $54,328,406 |

## NEEDS CATEGORIES

The following are recommended groupings of assessed needs by priority.

### Priority 1A: Short-Term Critical Needs

High priority items to preserve assets and meet minimum standards.

#### SAFETY

Observed structural concerns, large gaps in guardrails, and tripping hazards

#### FIRE LIFE SAFETY/CODE

Updates needed to fire alarm, emergency lighting, and emergency power

#### SEISMIC

Perform necessary investigations & evaluation to confirm what’s needed

#### ACCESSIBILITY

Updates needed to meet minimum needs:

- Accessible Route from parking areas to main entrance of buildings & level one of buildings

- One single use toilet

- Dual height drinking fountain

- Accessible Living Units

#### SECURITY

Updates needed to meet minimum needs:

- Secured/fenced site perimeter

- Buildings are secured/doors close

#### HAZARDOUS MATERIALS

- Remove hazardous materials observed to be cracked/friable, or damaged

- Remove hazardous materials identified as standing in the way of general maintenance

- Perform additional testing to confirm materials suspected to be hazardous

#### DEFERRED MAINTENANCE

Repair of problematic infrastructure & end of life replacements

### Priority 1B: Long-Term Critical Needs

Additional items needed to maintain assets and meet current code. The schedule for these items will be impacted by the outcome of the Long-Range Facility Planning process.

#### FIRE LIFE SAFETY/CODE

Egress hardware, fire sprinkler upgrades

#### SEISMIC

Upgrades pending outcome of further investigations

#### GENERAL MAINTENANCE

Patch, paint and repair items

#### DEFERRED MAINTENANCE

- Domestic water distribution

- Roof replacements anticipated in 5-10 years

- Exterior & interior maintenance & repairs

#### INDOOR AIR QUALITY AND VENTILATION

- Replace radiator units to provide ventilation

- Corresponding electrical panels & service upgrades

#### HAZARDOUS MATERIALS

Remove materials confirmed to be hazardous by testing

### Priority 2: Other Assessed Needs

For consideration as part of Capital Improvements projects based on outcome of the Long-Range Facility Planning process.

#### ACCESSIBILITY

Accessible route to all levels of building

#### SECURITY

Security alarm at each building

#### ENERGY

Window replacements Add roof & wall insulation Lighting upgrades to LED fixtures for improved light quality

#### DEFERRED MAINTENANCE

Remodel & repairs to vacant buildings

#### INDOOR AIR QUALITY AND VENTILATION

Add or replace cooling systems

#### HAZARDOUS MATERIALS

Remove confirmed hazardous materials as part of remodel and repairs to vacant buildings

#### SEISMIC

Upgrades as part of remodel and repairs to vacant buildings

## Summary of Recommendation

The following information represents how the costs of assessed needs are distributed.

### Residential

| Facility Number and Name | Total Assessed Needs |  |
| --- | --- | --- |
| 03 Peterson Hall |  | $12,727,085 |
| 05 Lindstrom Hall |  | $17,522,450 |
| 17 New Dorm |  | $1,834,853 |

### Educational

| Facility Number and Name | Total Assessed Needs |
| --- | --- |
| 02 Wallace Hall | $3,350,970 |
| 04 Kuenzi | $16,879,752 |
| 09 Hokanson Gym | $5,773,680 |
| 11 Peck Gym | $12,941,208 |
| 12 Ulmer | $9,608,625 |
| 13 Smith Hall | $22,538,736 |

### Student Support

| Facility Number and Name | Total Assessed Needs |
| --- | --- |
| 07 Clatterbuck | $18,520,488 |

### Facilities Support

| Facility Number and Name | Total Assessed Needs |  |
| --- | --- | --- |
| 08 Central Plant |  | $8,959,950 |

### Vacant

| Facility Number and Name | Total Assessed Needs |
| --- | --- |
| 01 Carpenter House & 14 Garage | $469,476 |
| 06 Tillinghast & 16 Carport | $1,143,180 |

### Campus Totals

| Total Assessed Needs | Assessed Needs escalated to mid-2027 |
| --- | --- |
| $54,328,406 | $70,386,138 |

# Assessment Summaries

## Site

Area: 37.3 Acres; Originally 52 Acres

Parking: 156 Total, Including (eight) Accessible Parking Spots

Address: 999 Locust Street NE, Salem Oregon 97301

Year Constructed: Campus established in 1909

### DESCRIPTION

Bounded by residential properties to north and west, and railroad tracks, commercial and residential to the south and east.

Plumbing:

- Waste: Original cast iron.

- Domestic Water: Original galvanized steel.

Mechanical: Central steam heating system distributed through a campus wide tunnel system.

Electrical: 120/240 and 208Y/120 Volt systems.

Telephone: VOIP through Project Music.

Data: Independent of phone system. Fiber connection outside of Smith.

Perimeter fencing and gates secure the campus.

Parking lots and access roads are paved, except gravel access road to the northern property.

Site Lighting:

- 40’ h Roadway Lights,

- 30’ h. Parking Lot Lights

- 20’ h. Walkways.

### Critical Needs Summary

#### SAFETY

- Lifting and cracked pavement.

- Outdated and damaged track and field equipment.

- An outdated emergency generator for the campus is located on the upper level of the Central Plant.

#### ACCESSIBILITY

- Paths between all buildings and parking need repair/replacement to proper slope.

- Curbs without curb ramps.

- Site signage needs updating to meet requirements.

- Playgrounds need updated surfacing and play equipment.

- The route to Grandstand and track is not accessible.

- Grandstand does not have an accessible viewing area or access to toilet rooms and concessions.

#### HAZARDOUS MATERIALS

Pipe insulation likely in tunnels – excluded from this study.

#### DEFERRED MAINTENANCE

- Storm drainage infrastructure gets clogged and creates wet/soggy areas, especially at area near Ulmer.

- Alligator cracks in areas of roadways and parking lots.

- Corroding domestic water supply piping.

#### FIRE LIFE SAFETY/CODE

No emergency lighting circuit for site lighting.

#### SECURITY

Leaning fence posts.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $4,407,756

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| G20 Site Improvements – Accessibility | Repair or regrade and replace non-compliant and cracked concrete pedestrian paving. | $454,487 |
| G20 Site Improvements – Accessibility | Update accessible parking to meet current requirements. | $333,113 |
| G20 Site Improvements – Accessibility | Add accessible ramps at walkways as part of accessible route | $63,788 |
| G20 Site Improvements – Security | Leaning fence posts and fabric along site perimeter & at playground. Repair 6’ chain link | $29,669 |
| G20 Site Improvements Accessibility | Replace directional & informational site signage | $148,838 |
| G20 Site Improvements – Accessibility | Replace playground surfacing and equipment at both playground areas | $364,000 |
| G20 Site Improvements – Safety | Gravel track is in disrepair and substandard to meeting safety standards | $654,885 |
| G20 Site Improvements – Safety | Replace soggy grass field with synthetic turf and subsurface drainage system | $1,600,613 |
| G30 Site Utilities – Deferred Maintenance | Original galvanized domestic water service piping is at end of life. Replace campus water distribution system. | $453,600 |
| G30 Site Utilities – Deferred Maintenance | Soggy grass area near Peck Gym. Repair storm pipe. | $21,263 |
| G30 Site Electrical Utilities – Fire Life Safety/Code | Provide emergency lighting circuit for site lighting | $28,350 |
| G30 Site Electrical Utilities – Safety | Replace emergency generator located at grade level | $255,150 |

#### PRIORITY 1AB: Long-Term Critical Needs

TOTAL: $561,414

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| G20 Site Improvements – Deferred Maintenance | Repair areas of asphalt paving indicated on diagram | $399,382 |
| G20 Site Improvements – Deferred Maintenance | Repair areas of concrete paving indicated on diagram | $80,692 |
| G20 Site Improvements – Deferred Maintenance | Replace flagpole | $11,340 |
| G20 Site Improvements – Accessibility | Replace sport court surfacing & striping | $70,000 |

#### PRIORITY 2: Other Assessed Needs

TOTAL $733,245

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| G20 Site Improvements – Accessibility | #16 Grandstand in poor condition and non-conforming. Replace with new Grandstand structure | $169,080 |
| G30 Site Electrical Utilities – Energy | Replace parking lot pole lighting with LED | $68,040 |
| G30 Site Electrical Utilities – Deferred Maintenance | Install field lighting to allow use of track and field safely at night | $496,125 |

## #1 Carpenter House

Use Category: Vacant

Area: 1,932 SF

Year Constructed Early: 1960’s

History/Use:

- 1960’s Used as Guest House

- 2020+- Vacant

Construction Type: Wood Frame Structure

### DESCRIPTION

One story wood frame structure on a full basement. Wood siding and Composition Roof. Building interior in state of partial demolition and unconditioned. #14 Garage is a freestanding structure of similar construction and condition to the house. The facility could be returned to use as a Guest House for students and parents with a complete remodel.

### Critical Needs Summary

#### SAFETY

Large gaps/openings at guardrails on exterior stair to basement are a safety hazard.

#### DEFERRED MAINTENANCE

As a VACANT building, the primary need is to preserve assets. The roof is reaching end of life, and the building exterior needs some repairs. Adding a heating & ventilating system is important to keep the building conditioned and preserved. No cooling is provided.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $6,237

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| C20 Stairs – Safety | Add perforated metal infill panels at exterior guardrail at steps to basement | $6,237 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $105,170

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Deferred Maintenance | Paint on wood siding is bubbling. Proper prep and repaint | $18,109 |
| B30 Roofing – Deferred Maintenance | Composition 15-20 years old. Replace end of life roof | $44,536 |
| D30 HVAC Systems – Deferred Maintenance | Radiators are dismantled. Install new unit ventilators | $42,525 |

#### PRIORITY 2: Other Assessed Needs

TOTAL $490,572

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation | $26,557 |
| B20 Exterior Enclosure – Energy | Original single pane windows. Cracked window putty. Replace exterior windows | $37,976 |
| B20 Exterior Enclosure – Accessibility | Threshold too high. Replace Main Entry door & frame | $4,253 |
| B20 Exterior Enclosure – Deferred Maintenance | Peeling paint on exterior doors. Repair, patch and paint | $2,977 |
| B20 Exterior Enclosure – Accessibility | Replace knob style door hardware at Main Entry | $2,127 |
| B30 Roofing – Energy | Insulation unlikely to meet code minimum. Install code minimum roof insulation | $9,723 |
| C10 Interior Construction – Deferred Maintenance | Investigate cause of cracks in basement walls. Repair, patch & paint | $4,962 |
| C10 Interior Construction – Accessibility | Replace interior doors & widen openings to provide an accessible route on level one | $20,554 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware | $5,224 |
| C10 Interior Construction – Accessibility | Replace kitchen to be accessible | $38,982 |
| C10 Interior Construction – Accessibility | Replace toilet rooms to be accessible | $46,778 |
| C20 Stairs – Accessibility | Demo and construct a new front porch and ramp | $43,136 |
| C20 Stairs – Deferred Maintenance | Replace worn carpet at stairs | $3,053 |
| C30 Interior Finishes – Deferred Maintenance | Repair water leak at tunnel entry | $6,379 |
| C30 Interior Finishes – Deferred Maintenance | Patch, repair and paint walls in basement | $8,628 |
| C30 Interior Finishes – Deferred Maintenance | Replace the damaged & worn carpet on level one | $8,560 |
| C30 Interior Finishes – Deferred Maintenance | Refinish hardwood floors on level one | $11,687 |
| C30 Interior Finishes – Accessibility | Replace sheet vinyl flooring in kitchen and toilet rooms | $5,916 |
| C30 Interior Finishes – Deferred Maintenance | Replace basement flooring | $67,535 |
| C30 Interior Finishes – Deferred Maintenance | Wet floor area in mechanical room. Investigate cause and repair | $6,848 |
| C30 Interior Finishes – Deferred Maintenance | Prep, patch, and paint all ceilings | $6,164 |
| D20 Plumbing Systems – Accessibility | Replace Kitchen & Toilet Room plumbing fixtures | $13,857 |
| D20 Plumbing Systems – Deferred Maintenance | Replace domestic water lines | 24,923 |
| D20 Plumbing Systems – Deferred Maintenance | Address drainage concern in basement | $9,214 |
| D30 HVAC Systems – Hazardous Materials | Abate & replace pipe insulation | $8,505 |
| D30 HVAC Systems – Deferred Maintenance | Replace pneumatic controls with digital | $16,433 |
| D50 Electrical Systems – Deferred Maintenance | Replace lighting | $7,797 |
| D50 Electrical Systems – Deferred Maintenance | Re-lamp basement lighting | $1,418 |
| D50 Electrical Systems – Deferred Maintenance | Rewire entire facility. Include emergency lighting circuit | $5,752 |
| D50 Electrical Systems – Deferred Maintenance | Upgrade fire alarm system | $9,998 |
| D50 Electrical Systems – Energy | Add occupancy sensors | $5,752 |
| E10 Equipment – Deferred Maintenance | Replace appliances | $8,222 |

## #2 Wallace Hall

Use Category: Educational

Area: 7,092 SF

Year Constructed: 1958

History/Use:

- 1958 – 2008+ Residence Hall for Children

- 2008+ – Present OSD Adult Transition Program

Construction Type: Wood Frame Structure

### DESCRIPTION

One story wood frame structure. Painted concrete exterior and single ply membrane Roof.9 Rooms centered on a common living room space with shared toilet rooms. Full kitchen, dining room and laundry. Steam radiators/no cooling.

### Critical Needs Summary

#### ACCESSIBILITY

Door openings along the accessible route to primary use areas are too narrow.

Door hardware repairs & upgrades needed along accessible route.

No accessible toilet rooms.

The kitchen is not accessible.

#### FIRE LIFE SAFETY/CODE

Emergency lighting may be needed.

Outdated egress door hardware.

#### HAZARDOUS MATERIALS

Cracked 9x9 floor tiles exposed. Additional materials are suspected to have asbestos and stand in the way of ongoing maintenance.

#### DEFERRED MAINTENANCE

Roof is reaching life expectancy.

Problematic pneumatic controls.

All plumbing fixtures are obsolete, worn and stained and child size.

Aging domestic water, sanitary and storm drainage systems.

Older Electrical panel & service.

#### INDOOR AIR QUALITY & VENTILATION

Radiant heaters do not provide ventilation or cooling. Condensation on windows.

#### SEISMIC

Evaluation is needed to confirm the extent of seismic deficiencies.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $406,630

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Accessibility | Provide automatic door opener at main entrance & replace knob hardware | $8,505 |
| C10 Interior Construction – Accessibility | Widen and replace interior doors along accessible route | $107,377 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware at interior doors along accessible route. MISSING | $14,800 |
| C10 Interior Construction – Accessibility | Interior room signage | $4,964 |
| C30 Interior Finishes – Accessibility | Ceramic wall tile as part of Toilet Room remodel | $15,026 |
| C30 Interior Finishes – Hazardous Materials | Abate cracked/friable vat & replace with VCT flooring | $49,762 |
| C30 Interior Finishes – Accessibility | Replace rubber base as part of flooring replacement | $8,051 |
| C30 Interior Finishes – Accessibility | Ceramic floor tile as part of Toilet Room remodel | $9,214 |
| D20 Plumbing Fixtures – Accessibility | New plumbing fixtures as part of Toilet Room remodel | $32,178 |
| D20 Plumbing Fixtures – Accessibility | Replace drinking fountain with dual height | $7,938 |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital | $75,398 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit | $2,128 |
| E10 Equipment – Accessibility | Replace appliances as part of Kitchen remodel | $14,672 |
| E10 Equipment – Accessibility | Replace toilet accessories as part of Toilet Room remodel | $2,524 |
| E10 Equipment – Accessibility | Replace toilet partitions as part of Toilet Room remodel | $15,026 |
| E20 Furnishings – Accessibility | Replace kitchen cabinets as part of Kitchen remodel | $39,067 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $1,136,707

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Seismic | Glulam beams & 2x decking. Add plywood sheathing | $31,850 |
| B10 Superstructure – Seismic | Install roof to exterior wall connections and associated costs | $63,749 |
| B20 Exterior Enclosure – Seismic | Add shear to exterior concrete walls with texture surface and paint | $160,745 |
| B30 Roofing – Deferred Maintenance (Energy) | Replace membrane roofing system. Includes add code minimum insulation | $366,821 |
| B30 Roofing – General Maintenance | Clean skylights | $700 |
| C30 Interior Finishes – Hazardous Materials | Abate plaster if found to contain asbestos. Add wallboard and paint | $184,477 |
| C30 Interior Finishes – Deferred Maintenance | Replace worn carpet | $22,527 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace glue-up ceiling tile if found to contain asbestos | $49,762 |
| C30 Interior Finishes – Deferred Maintenance | Abate & replace painted gypsum board ceilings if found to contain asbestos | $60,319 |
| D20 Plumbing Systems – Deferred Maintenance | Replace corroded domestic waterlines | $150,794 |
| D20 Plumbing Systems – General Maintenance | Repair overflowing gutter & downspout | $1,531 |
| D30 HVAC Systems – Deferred Maintenance | Repair leak in ducts | $2,835 |
| D30 HVAC Systems – Deferred Maintenance | Add lagging to pipe hangers and fittings | $15,081 |
| D30 HVAC Systems – Deferred Maintenance | Replace broken baseboard heaters | $17,719 |
| D30 HVAC Systems – Indoor Air Quality/Ventilation | Replace loud exhaust fan | $4,962 |
| D40 Fire Protection Systems – Deferred Maintenance | Repair leak in fire sprinkler system located in basement near fire riser | $2,835 |

#### PRIORITY 2 Other Assessed Needs

TOTAL: $513,306

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation | $134,215 |
| B20 Exterior Enclosure – Energy | Original single pane windows. Cracked window putty. Replace exterior windows | $281,781 |
| B20 Exterior Enclosure – Energy | Replace inefficient exterior doors (not main entry) | $14,530 |
| B30 Roofing – Energy | Insulation unlikely to meet code minimum. Install code minimum roof insulation. Included as part of roof replacement | See 1B |
| D50 Electrical Systems – Energy | Replace interior lighting in skylights with LED | $13,573 |
| D50 Electrical Systems – Energy | Replace interior lighting with LED | $35,187 |
| D50 Electrical Systems – Energy | Replace exterior lighting | $5,670 |
| D50 Electrical Systems – Security | Install intrusion alarm system | $14,175 |
| D50 Electrical Systems – Energy | Add occupancy sensors | $14,175 |

## #3 Peterson Hall

Use Category: Residential

Area: 24,173 SF

Year Constructed: 1962

History/Use: 1962 - Present Girl’s Residence Hall

Construction Type: Wood Frame Structure

### DESCRIPTION

One story wood frame structure on a partial basement. Brick veneer with painted stucco panels and single ply membrane Roof. Exposed wood structure over the entry and gathering space with common area kitchen. Residential units including single rooms with shared bath and apartment style units. Laundry, Recreation, and Mechanical Rooms are located in the basement. Capacity to house up to 90 occupants. Steam radiators/No cooling.

### Critical Needs Summary

#### SAFETY

Large gaps/openings at guardrails on exterior stair to basement are a safety hazard.

#### ACCESSIBILITY

Door openings along the accessible route to primary use areas are too narrow.

Door hardware repairs and upgrades needed at main entry and along accessible route.

Residential units are not accessible.

Common area Kitchen is not accessible.

Basement is not accessible and currently has a Program accessed by students and staff.

#### FIRE LIFE SAFETY/CODE

Emergency lighting may be needed.

Outdated egress door hardware.

#### SEISMIC

Evaluation needed to confirm extent of seismic deficiencies.

#### HAZARDOUS MATERIALS

Cracked 9x9 floor tiles exposed and under worn carpet areas.

Damaged pipe insulation.

Additional materials are suspect to have asbestos and stand in the way of ongoing maintenance.

#### DEFERRED MAINTENANCE

- Roof is reaching life expectancy.

- Problematic pneumatic controls.

- All plumbing fixtures are obsolete, worn and stained.

- Aging domestic water, sanitary and storm drainage systems.

- Older Electrical panel & service.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $848,149

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Accessibility | Replace automatic door opener at main entrance | $6,521 |
| C10 Interior Construction – Accessibility | Widen and replace interior doors along accessible route | $45,077 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware at interior doors along accessible route | $49,613 |
| C10 Interior Construction – Accessibility | Interior room signage | $16,921 |
| C10 Interior Construction – Accessibility | Remodel Residential Unit Toilet Rooms | $51,030 |
| C20 Stairs – Safety | Add perforated metal infill panels at exterior guardrail at steps to basement | $12,500 |
| C30 Interior Finishes – Hazardous Materials | Abate cracked/friable vat & replace with VCT flooring, including areas under carpet | $84,809 |
| C30 Interior Finishes – Deferred Maintenance | Replace rubber base as part of flooring replacement | $19,617 |
| D30 HVAC Systems – Hazardous Materials | Abate and replace damaged pipe insulation | $40,824 |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital | $256,991 |
| D50 Electrical Systems – Safety | Provide GFI circuits | $3,544 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit | $7,252 |
| E10 Equipment – Accessibility | New toilet accessories at remodeled accessible toilet rooms | $21,263 |
| E10 Equipment – Accessibility | Replace appliances and remodel kitchens at accessible residential units and common area | $232,187 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $4,064,506

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Seismic | Glulam beams & 2x decking. Add plywood sheathing | $77,458 |
| B10 Superstructure – Seismic | Install roof to exterior wall connections and associated costs. | $128,029 |
| B20 Exterior Enclosure – Seismic | Add shear to exterior walls | $167,974 |
| B20 Exterior Enclosure – General Maintenance | Clean, prep and Paint Wood Siding | $4,761 |
| B20 Exterior Enclosure – Seismic | Add helical ties to brick veneer | $15,959 |
| B20 Exterior Enclosure – Fire Life Safety/Code | Replace egress hardware | $12,096 |
| B30 Roofing – Deferred Maintenance (Energy) | Replace membrane roofing system. Includes add code minimum insulation | $852,031 |
| C10 Interior Construction – Deferred Maintenance | Repair and refinish interior doors | $87,885 |
| C20 Stairs – Fire Life Safety/Code | Replace handrails at stairs to basement | $6,748 |
| C30 Interior Finishes – Hazardous Materials | Abate plaster if found to contain asbestos. Add wall board and paint | $597,055 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace ceiling tile if found to contain asbestos | $226,153 |
| C30 Interior Finishes – Deferred Maintenance | Replace worn carpet | $160,363 |
| D20 Plumbing Systems – Deferred Maintenance | Replace obsolete and stained plumbing fixtures | $284,776 |
| D20 Plumbing Systems – Deferred Maintenance | Replace corroded domestic waterlines | $462,583 |
| D20 Plumbing Systems – Deferred Maintenance | System backs up due to clogging and corrosion. Replace original sanitary piping | $188,461 |
| D20 Plumbing Systems – Deferred Maintenance | Repair range of exterior drainage issues including clogged drain at exterior stairwell | $17,010 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Replace original radiators with unit ventilators that provide cooling | $548,245 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Check operation of all exhaust fans and tie into central exhaust system | $102,797 |
| D40 Fire Protection Systems – Deferred Maintenance | Repair leak in fire sprinkler system located in basement near fire riser | $2,835 |
| D50 Electrical Systems – Fire Life Safety/Code | Upgrade electrical panel, especially with HVAC upgrades | $71,958 |
| E20 Furnishings – Deferred Maintenance | Replace bathroom vanities in residential units | $49,329 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $1,008,651

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| A20 Basement Construction – Energy | Patch and paint CMU walls in basement | $23,567 |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation | $69,011 |
| B20 Exterior Enclosure – Energy | Original single pane windows. Broken screens. Replace exterior windows | $434,507 |
| B20 Exterior Enclosure – Energy | Replace inefficient exterior doors (not main entry) | $48,366 |
| B30 Roofing – Energy | Insulation unlikely to meet code minimum. Install code minimum roof insulation. Included as part of roof replacement. | See 1B |
| C20 Stairs – Accessibility | Add elevator to access basement | $313,268 |
| D50 Electrical Systems – Energy | Replace lighting with LED fixtures | $42,833 |
| D50 Electrical Systems – Security | Install intrusion alarm system | $34,266 |
| D50 Electrical Systems – Energy | Add occupancy sensors | $42,833 |

## #4 Kuenzi Hall

Use Category: Educational

Area: 32,904 SF

Year Constructed: 1940’s

History/Use:

- 1940’s – 2010+/- Classroom and Dormitory Building

- 2013 – Present Charter Elementary School and Museum

Construction Type: Concrete

### DESCRIPTION

One story wood frame structure on a partial basement.

8” thick concrete walls with masonry veneer and asphalt shingle roof with original copper perimeter and dormers.

The level one Classroom areas are occupied by students and staff outside of OSD. Locker rooms serve as storage.

The former dormitory houses the OSD Museum and Archives.

Basement level Weight Room and separate Student Lounge space used by OSD students.

New boiler in basement. Original Steam radiators/several window air conditioning units as cooling.

### Critical Needs Summary

#### SAFETY

Gap at pedestrian bridge connection as a structural concern.

Make-shift Acoustic panels as a potential fire hazard.

Obstructed access to original electrical panels as a fire hazard.

Large gaps/openings at guardrails on exterior stair to basement are a safety hazard.

#### ACCESSIBILITY

Narrow door openings, door hardware repairs & upgrades needed at main entry and along accessible route.

No accessible toilets.

Accessible egress needs review.

Weight Room in basement is not accessible and a 4” H. platform in Student Lounge prevents access by all students.

#### SEISMIC

Evaluation needed to confirm extent of seismic deficiencies.

#### FIRE LIFE SAFETY/CODE

Obsolete electrical panels.

Emergency lighting may be needed.

Outdated egress door hardware.

#### DEFERRED MAINTENANCE

End of life Roof with active leaks identified at transition of copper/composition shingles.

All plumbing fixtures are obsolete, worn and stained.

Aging domestic water, sanitary and storm drainage systems.

#### INDOOR AIR QUALITY & VENTILATION

Radiant heaters do not provide ventilation or cooling.

#### HAZARDOUS MATERIALS

Cracked 9x9 floor tiles exposed.

Additional materials are suspect to have asbestos and stand in the way of ongoing repairs.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $2,188,081

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Deferred Maintenance (Seismic) | Add plywood sheathing as part of roof replacement | $93,478 |
| B10 Superstructure – Safety | Repair gap at pedestrian bridge connection | $35,580 |
| B20 Exterior Enclosure – Accessibility | Replace door hardware at Main Entrance | $5,211 |
| B30 Roofing – Deferred Maintenance (Energy) | Replace end of life composite shingles with copper perimeter & dormers. Include roof insulation | $938,925 |
| C10 Interior Construction – Accessibility | Widen and replace interior doors along accessible route | $313,438 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware at interior doors along accessible route | $24,098 |
| C10 Interior Construction – Accessibility | Interior room signage | $23,033 |
| C10 Interior Construction – Accessibility | Add single use accessible toilet room | $106,313 |
| C20 Stairs – Safety | Add infill panels at open guardrails at stair to basement and exterior. | $6,237 |
| C30 Interior Finishes – Safety | Replace make-shift acoustical wall panels | $16,302 |
| C30 Interior Finishes – Hazardous Materials | Abate cracked/friable vat & replace with VCT flooring at areas under carpet | $62,618 |
| C30 Interior Finishes – Hazardous Materials | Abate cracked/friable vat & replace with VCT flooring | $115,439 |
| C30 Interior Finishes – Deferred Maintenance | Replace rubber base as part of flooring replacement | $9,835 |
| D20 Plumbing Systems – Accessibility | Install dual height drinking fountain | $7,938 |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital. | $349,811 |
| D50 Electrical Systems – Fire Life Safety/Code | Upgrade obsolete electrical panels, especially with HVAC upgrades | $69,954 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit | $9,871 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $3,906,569

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| A10 Foundations – Deferred Maintenance | Patch and repair spalling concrete walls | $7,797 |
| A20 Basement Construction – General Maintenance | Patch, repair & paint spalling concrete walls. | $51,000 |
| B10 Superstructure – Seismic | Install roof to exterior wall connections and associated costs | $181,044 |
| B20 Exterior Enclosure – Deferred Maintenance | Repair cracks in brick at outside corners. Clean and repair masonry | $99,622 |
| B20 Exterior Enclosure – Fire life Safety/Code | Replace egress door hardware | $34,616 |
| B30 Roofing – Seismic | Replace masonry chimneys with wood construction | $28,350 |
| C10 Interior Construction – Seismic | Replace clay tile walls supporting concrete beams at corridors | $490,757 |
| C20 Stairs – Fire Life Safety/Code | Replace handrails at stairs to basement and exterior | $9,871 |
| C30 Interior Finishes – Hazardous Materials | Abate plaster if found to contain asbestos. Add wall board and paint | $525,212 |
| C30 Interior Finishes – Deferred Maintenance | Replace flooring as part of multi-user toilet room remodel | $58,303 |
| C30 Interior Finishes – Deferred Maintenance | Patch, repair, and paint ceilings | $11,662 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace ceiling tile if found to contain asbestos | $153,918 |
| D20 Plumbing Systems – Deferred Maintenance | Replace obsolete and stained plumbing fixtures | $183,922 |
| D20 Plumbing Systems – Deferred Maintenance | Replace corroded domestic waterlines | $279,850 |
| D20 Plumbing Systems – Deferred Maintenance | Unclog drains & replace cast iron downspout boot | $6,309 |
| D30 HVAC Systems – General Maintenance | Investigate and repair intermittent issue with central boiler unit installed in 2015 | $7,088 |
| D30 HVAC Systems – Hazardous Materials | Replace pipe insulation | $54,432 |
| D30 HVAC Systems – Indoor Air Quality/Ventilation | Replace broken exhaust fans | $14,175 |
| D30 HVAC Systems – Indoor Air Quality/Ventilation | Replace original steam radiators with units that provide ventilation | $699,622 |
| D40 Fire Protection – Fire Life Safety/Code | Replace original fire sprinkler system | $361,944 |
| D50 Electrical Systems – Deferred Maintenance | Original conductors. Rewire facility | $72,296 |
| D50 Electrical Systems – Deferred Maintenance | Upgrade electrical panel, especially with HVAC upgrades | $69,954 |
| E10 Equipment – Deferred Maintenance | Replace toilet partitions as part of multi-user toilet room remodel | $42,525 |
| E20 Furnishings – Deferred Maintenance | Replace casework in Classrooms | $510,300 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $2,382,422

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation | $257,133 |
| B20 Exterior Enclosure – Energy | Original single pane windows in Classroom areas. Replace exterior windows | $536,352 |
| B20 Exterior Enclosure – Energy | Replace inefficient exterior doors | $82,769 |
| B30 Roofing – Energy | Insulation unlikely to meet code minimum. Install code minimum roof insulation. Included as part of roof replacement | See 1A |
| C20 Stairs – Accessibility | Add ramp to access Weight Room in basement | $16,614 |
| C30 Interior Finishes – Deferred Maintenance | Remodel abandoned Locker Rooms, include accessible changing room | $17,010 |
| C30 Interior Finishes – Accessibility | Remove platform in basement Student Lounge and replace with VCT | $10,332 |
| D30 HVAC Systems – Energy | Install cooling system to replace window air conditioning units | $1,166,036 |
| D50 Electrical Systems – Energy | Replace inefficient lighting with LED | $214,551 |
| D50 Electrical Systems – Security | Install intrusion alarm system | $34,982 |
| D50 Electrical Systems – Energy | Add occupancy sensors | $46,643 |

## #5 Lindstrom Hall

Use Category: Residential

Area: 31,100 SF Main Level; 25,000 SF Basement

Year Constructed: 1957

History/Use: 1957 - Present Boys Dormitory Student Run Halloween Haunted House in Basement

Construction Type: Concrete and Wood Frame Structure

### DESCRIPTION

Concrete exterior walls and wood frame structure with basement

Built-up roof.

Common areas with dormitory rooms on central corridor at main level

Radiant heaters with no ventilation or cooling systems.

### Critical Needs Summary

#### SAFETY

Large gaps/openings at guardrails at interior stair to basement are a safety hazard.

#### ACCESSIBILITY

Door hardware upgrades needed along accessible route.

Exterior main entry ramp does not meet current accessibility code.

Common area kitchen is not accessible.

Residential unit toilet rooms are not accessible.

Basement is not accessible from main level, however, does not have program accessed by students and staff.

#### FIRE LIFE SAFETY/CODE

Emergency lighting may be needed.

#### SEISMIC

Evaluation needed to confirm extent of seismic deficiencies.

#### HAZARDOUS MATERIALS

9x9 asbestos floor tiles exposed and under worn carpet areas.

Cracked asbestos flooring in some toilet rooms.

Damaged asbestos pipe insulation.

Additional materials are suspect to have asbestos and stand in the way of ongoing maintenance.

#### DEFERRED MAINTENANCE

Problematic pneumatic controls.

All plumbing fixtures are obsolete, worn and stained.

Aging domestic water, sanitary and storm drainage systems.

Older Electrical panel & service.

Dormitory room cabinets in poor condition.

#### INDOOR AIR QUALITY & VENTILATION

Radiant heaters do not provide ventilation or cooling.

Common kitchen and laundry areas need exhaust fans replaced

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $2,146,999

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Deferred Maintenance (Accessibility) | Replace all exterior doors including door hardware and thresholds | $76,290 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware at interior doors along accessible route | $107,022 |
| C20 Ramps – Fire Life Safety/Code (Accessibility) | Install new or modify existing guardrails and handrails at exterior ramps to meet current code | $5,337 |
| C20 Stairs – Fire Life Safety/Code | Install new or modify existing guardrails and handrails at interior stairs to meet current code | $34,846 |
| C20 Stairs – Hazardous Materials (Deferred Maintenance) | Abate vinyl asbestos tile at interior stairs and remove entry mat and replace with new flooring | $12,075 |
| C10 Interior Construction – Accessibility | Interior room signage | $31,570 |
| C30 Interior Finishes – Hazardous Materials | Abate all asbestos floor tile and install new VCT | $193,310 |
| C30 Interior Finishes – Hazardous Materials | Abate all asbestos floor tile and replace carpet | $454,589 |
| C30 Interior Finishes – Hazardous Materials | Abate resilient asbestos flooring in all toilet rooms | $97,632 |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital | $546,730 |
| D30 HVAC Systems – Hazardous Materials | Abate asbestos pipe insulation | $429,574 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit | $13,530 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $12,446,940

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Seismic | Strengthen concrete columns at covered area | $74,419 |
| B10 Superstructure – Seismic | Install plywood sheathing at roof | $131,661 |
| B10 Superstructure – Seismic | Install roof to exterior wall connections and associated costs | $198,167 |
| B10 Superstructure – Seismic | Reinforce exterior concrete walls | $1,180,778 |
| B20 Exterior Enclosure – Deferred Maintenance (Energy) | Replace all windows | $839,742 |
| B30 Roofing – Deferred Maintenance (Energy) | Replace membrane roofing system. Includes add code minimum insulation | $1,164,133 |
| C10 Interior Construction – Seismic | Reinforce or remove cmu partition walls in basement | $340,200 |
| C30 Interior Finishes – Hazardous Materials | Abate plaster if found to contain asbestos. Add wall board and paint | $1,415,562 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace ceiling tile if found to contain asbestos. | $322,182 |
| D20 Plumbing Systems – Accessibility (Deferred Maintenance) | Replace all faucets and sinks | $420,289 |
| D20 Plumbing Systems – Deferred Maintenance | Replace original corroded domestic waterlines | $624,834 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation (Energy) | Install ventilation and heating system | $2,733,649 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Install cooling system | $1,562,085 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Replace kitchen and laundry exhaust fans | $8,505 |
| D50 Electrical Systems – Fire Life Safety/Code | Upgrade electrical panel, especially with HVAC upgrades | $144,494 |
| E10 Equipment – Accessibility | Replace appliances and remodel common kitchen | $219,713 |
| E10 Equipment – Accessibility (Deferred Maintenance) | Remodel all dormitory toilet rooms to be accessible | $637,875 |
| E20 Furnishings – Deferred Maintenance | Replace all dormitory room built-in cabinets | $428,652 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $370,085

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| D50 Electrical Systems – Energy | Replace lighting with LED’s | $243,540 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $52,345 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $74,200 |

## #6 Tillinghast Hall

Use Category Vacant

Area 2,920 SF

Year Constructed 1914

History/Use 1914 Administration, Present Vacant

Construction Type Wood Frame Structure

### DESCRIPTION

One story wood frame structure.

Brick and wood siding and asphalt shingle roof.

Vacant.

Basement part of campus tunnel system for hot water pipes from central boiler and campus IT system.

### Critical Needs Summary

#### FIRE LIFE SAFETY/CODE

Emergency lighting may need to be added.

#### DEFERRED MAINTENANCE

As a VACANT building, the primary need is to preserve assets.

All exterior wood trim and siding needs to be painted to protect from weather.

Water ponding in basement and tunnel near campus IT equipment.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $25,349

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| A20 Basement Construction – Deferred Maintenance | Investigate cause of water ponding in basement and adjacent utility tunnel and repair. | $21,263 |
| B20 Exterior Enclosure – Deferred Maintenance | Repair and paint all exterior wood shingles, trim, and facias. | $3,210 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit. | $876 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $1,095,006

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Seismic | Install plywood sheathing at first and second floors. | $13,673 |
| B10 Superstructure – Seismic | Install plywood sheathing at roof. | $11,306 |
| B10 Superstructure – Seismic | Install roof and floor to wall connections. Install wall to foundation connections. | $47,310 |
| B20 Exterior Enclosure – Seismic | Reinforce and repair cracks in unreinforced brick masonry and concrete porch wall. | $14,958 |
| B20 Exterior Enclosure – Deferred Maintenance | Replace all original wood single pane windows. | $100,575 |
| B20 Exterior Enclosure – Accessibility (Deferred Maintenance) | Repair or replace all original wood exterior doors and hardware. | $12,758 |
| B20 Exterior Enclosure – Energy | Add insulation in roof attic. | $15,417 |
| B20 Exterior Enclosure – Energy | Add insulation at exterior walls. | $25,859 |
| B30 Roofing – Deferred Maintenance | Replace asphalt shingle roofing system. | $63,328 |
| B30 Roofing – Seismic | Reinforce or remove two unreinforced masonry chimneys. | $24,098 |
| C10 Interior Construction – Deferred Maintenance | Repair and paint plaster wall surfaces. | $24,470 |
| C10 Interior Construction – Deferred Maintenance | Repair and paint interior wood doors. | $32,533 |
| C10 Interior Construction – Accessibility | Replace all interior door hardware. | $5,000 |
| C10 Interior Construction – Accessibility | Interior room signage. | $2,044 |
| C20 Ramp and Stairs – Accessibility | Replace exterior concrete ramp and handrails at main entry stairs. | $28,350 |
| C20 Stairs – Fire Life Safety/Code (Accessibility) | Replace exterior wood stair to second floor. | $30,000 |
| C30 Interior Finishes – Deferred Maintenance | Repair and paint interior wood trim. | $12,652 |
| C30 Interior Finishes – Deferred Maintenance | Replace worn carpet or refinish and repair hardwood floors. | $23,283 |
| C30 Interior Finishes – Hazardous Materials | Abate asbestos vinyl tile in kitchen and bathrooms and install resilient flooring. | $5,175 |
| C30 Interior Finishes – Deferred Maintenance | Paint all plaster ceilings. | $9,314 |
| D10 Elevators and Lifts – Accessibility | Install elevator. | $354,375 |
| D20 Plumbing Systems – Accessibility (Deferred Maintenance) | Replace all toilet room and kitchen plumbing fixtures. | $6,592 |
| D20 Plumbing Systems – Deferred Maintenance | Replace original corroded domestic waterlines. | $42,635 |
| D20 Plumbing Systems – Deferred Maintenance | Replace original corroding sanitary piping. | $20,696 |
| D20 Plumbing Systems – Deferred Maintenance | Replace all gutters and downspouts. | $14,459 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Install central ventilation, heating, and air conditioning system. | $82,782 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Install exhaust fans in toilet rooms. | $2,765 |
| D50 Electrical Systems – Energy | Replace lighting with LED fixtures. | $27,940 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $7,244 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $14,487 |
| E10 Equipment – Accessibility | Replace toilet room accessories. | $3,828 |
| E20 Furnishings – Accessibility | Replace all cabinets. | $15,000 |

## #7 Clatterbuck Building

Use Category Student Support

Area 32,664 SF

Year Constructed 1971

History/Use 1971 - Present Dining Hall and Infirmary for OSD

Construction Type Wood Frame Structure

### DESCRIPTION

One story wood frame structure on a full basement.

Brick veneer with painted panels and metal mansard roof at perimeter with single ply membrane Roof.

Exposed wood structure over the entry and dining space with commercial kitchen.

Infirmary/health center with separate entry.

Main storehouse for the campus and unused locker rooms with access for the track are located in the basement. Only elevator on campus

Unit ventilators/No cooling.

### Critical Needs Summary

#### SAFETY

Visible cracks on interior and gaps at the exterior of the infirmary wing indicate movement.

Large gaps/openings at guardrails on stairs to basement are a safety hazard.

#### ACCESSIBILITY

Door openings along accessible route to primary use areas are too narrow.

Door hardware repairs & upgrades needed at main entry and along accessible route.

#### FIRE LIFE SAFETY/CODE

Emergency lighting may be needed.

Outdated egress door hardware.

#### SEISMIC

Evaluation needed to confirm extent of seismic deficiencies.

#### HAZARDOUS MATERIALS

Suspect 12x12 floor tiles.

Suspect pipe insulation.

Additional materials are suspect to have asbestos and stand in the way of ongoing maintenance.

#### DEFERRED MAINTENANCE

Exposed ductwork on roof is rusted, damaged and impacting efficiency.

Problematic air handlers in mechanical penthouse on roof.

#### INDOOR AIR QUALITY & VENTILATION

Older split system chiller tied to pneumatic controls.

Dirty Soot-stained supply and return air vents.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $1,453,951

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| A10 Foundations – Safety | Investigate and repair cracks in foundation. | $212,625 |
| B10 Superstructure – Safety | Repair sunken slab area at Infirmary entrance. | $21,263 |
| B20 Exterior Enclosure – Safety | Investigate shifting of masonry. | $7,797 |
| C10 Interior Construction – Accessibility | Widen and replace interior doors along accessible route. | $124,918 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware at interior doors along accessible route. | $17,719 |
| C10 Interior Construction – Accessibility | Interior Room Signs. | $22,865 |
| C20 Stairs – Safety | Add perforated metal infill panels at exterior guardrail at steps to basement. | $6,237 |
| D30 HVAC Systems – Deferred Maintenance | Replace damaged and rusty rooftop ductwork. | $81,029 |
| D30 HVAC Systems – Deferred Maintenance | Remove/replace AHU & new pan. Replace rooftop mechanical penthouse. | $602,438 |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital. | $347,260 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $890,880

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Seismic | Glulam beams & 2x decking. Verify plywood decking was installed as part of recent roof replacement. | $0 |
| B20 Exterior Enclosure – Seismic | Masonry pier connections. | $24,807 |
| B20 Exterior Enclosure – General Maintenance | Clean and seal brick veneer. MISSING | $32,664 |
| B20 Exterior Enclosure – Fire Life Safety/Code | Replace egress hardware. | $3,360 |
| B30 Roofing – Deferred Maintenance | Clean metal mansard roofing. | $34,875 |
| C10 Interior Construction – Seismic | Strengthen wall to roof connection at interior masonry walls. | $23,531 |
| C10 Interior Construction – Seismic | Add interior shear walls between piers. | $85,088 |
| C20 Stairs – General Maintenance | Re-paint chipped exterior handrails. | $397 |
| C30 Interior Finishes – Hazardous Materials | Abate plaster if found to contain asbestos. Add wall board and paint. | $435,337 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace floor tile if found to contain asbestos. | $76,400 |
| C30 Interior Finishes – General Maintenance | Repair and clean quarry tile in kitchen. | $5,742 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace gypsum board ceilings if found to contain asbestos. | $69,454 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace ceiling tile if found to contain asbestos. | $76,400 |
| D20 Plumbing Systems – Deferred Maintenance | Repair and reattach straps at scuppers. | $1,418 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Clean and repair unit ventilators at dining. | $7,088 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Clean and repair exhaust fans. | $4,962 |
| D50 Electrical Systems – Fire Life Safety/Code | Upgrade electrical panel. | $1,064 |
| E10 Equipment – Fire Life Safety/Code | Replace wood countertop in kitchen. | $8,293 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $2,163,726

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation. | $98,314 |
| B20 Exterior Enclosure – Energy | Rusty frame single pane windows. Replace exterior windows. | $513,481 |
| B20 Exterior Enclosure – Energy | Replace inefficient exterior doors (not main entry). | $51,002 |
| B30 Roofing – Energy | Insulation unlikely to meet code minimum. Install code minimum roof insulation. Included as part of roof replacement. | $114,995 |
| C30 Interior Finishes – Accessibility | Add single use toilet room and change room in Locker rooms for use by Track & Field. | $40,000 |
| D20 Plumbing Systems – Deferred Maintenance | Remove unused plumbing fixtures. Remodel to storage room. | $32,249 |
| D30 HVAC Systems – Energy | Replace cooling system. | $1,018,629 |
| D50 Electrical Systems – Energy | Replace lighting. | $208,357 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $34,727 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $46,302 |
| E20 Furnishings – Accessibility | Replace casework in health center to meet accessibility requirements. | $5,670 |

## #8 Central Plant

Use Category Facilities Support

Area 13,274 SF

Year Constructed 1950 + 1961 Addition

History/Use

1950 Central Heat Plant for Campus

1961 Added Maintenance Area

Construction Type Original: Unreinforced masonry. Addition: Reinforced Concrete floor, roof and walls.

### DESCRIPTION

One story with mezzanine and exterior pedestrian bridge connection to Hokanson Gym.

Painted concrete exterior and single ply membrane Roof.

Provides most of the heat and electrical needs for the campus distributed through the campus tunnel system.

Houses the emergency generator for the campus.

### Critical Needs Summary

#### SAFETY

Large gaps/openings at guardrails on exterior stair to basement are a safety hazard.

Loose guardrails at pedestrian bridge.

#### ACCESSIBILITY

Building is not required to be accessed by the public.

No accessible toilet room or route.

#### HAZARDOUS MATERIALS

Pipe insulation.

Additional materials are suspect to have asbestos and stand in the way of ongoing maintenance.

#### DEFERRED MAINTENANCE

Water is ponding and moss growing on end-of-life Roof.

All plumbing fixtures are obsolete, worn and stained.

Aging domestic water, sanitary and storm drainage systems.

#### FIRE LIFE SAFETY/CODE

Emergency lighting may be needed.

#### SEISMIC

Evaluation needed to confirm the extent of seismic deficiencies.

Provides central services to other essential buildings on campus.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $353,035

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B30 Roofing – Deferred Maintenance | Replace end of life built up with membrane roofing. | $314,960 |
| C20 Stairs – Safety | Add perforated metal infill panels at mezzanine guardrail. | $17,691 |
| C20 Stairs – Safety | Repair loose guardrails at pedestrian bridge. | $9,314 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit. | $3,982 |
| D50 Electrical Systems – Fire Life Safety/Code | Replace j-box covers, provide GFI receptacles. | $7,088 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $1,739,560

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| A20 Basement Construction – Deferred Maintenance | Investigate water leak at tunnel and repair. | $7,088 |
| B10 Superstructure – Seismic | Seismic reinforcing of mezzanine slab and pedestrian bridge. | $388,269 |
| B10 Superstructure – Seismic | Reinforce roof structure. | $510,300 |
| B10 Superstructure – Seismic | Roof to wall connections. | $59,535 |
| B20 Exterior Enclosure – Seismic | Strengthen unreinforced walls. | $241,920 |
| B20 Exterior Enclosure – Seismic | Strengthen unreinforced walls. | $70,875 |
| C10 Interior Construction – Seismic | Strengthen CMU walls. | $42,525 |
| C10 Interior Construction – General Maintenance | Patch, repair and paint interior doors. | $4,750 |
| C20 Stairs – Fire Life Safety/Code | Replace open riser metal stair to mezzanine. | $20,838 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace wallboard and plaster if found to contain asbestos. | $17,861 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace 9x9 floor tiles with VCT. | $31,048 |
| C30 Interior Finishes – General Maintenance | Clean and recoat concrete floors. | $34,340 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace gypsum board ceilings if found to contain asbestos. | $2,352 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace glue-up ceiling tile if found to contain asbestos. | $23,287 |
| C30 Interior Finishes – General Maintenance | Clean and paint open to structure ceilings. | $48,922 |
| D20 Plumbing Systems – Deferred Maintenance | Replace stained and obsolete plumbing fixtures. | $30,051 |
| D20 Plumbing Systems – Deferred Maintenance | Replace corroded domestic waterlines. | $56,450 |
| D30 HVAC Systems – Hazardous Materials | Replace pipe insulation. | $2,835 |
| D50 Electrical Systems – Deferred Maintenance | Upgrade electrical service as impacted by other facilities on campus. | $142,061 |
| E10 Equipment – Deferred Maintenance | Replace toilet accessories. | $4,253 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $503,419

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation. | $169,080 |
| B20 Exterior Enclosure – Energy | Original single pane wood windows. Replace exterior windows. | $165,113 |
| B20 Exterior Enclosure – Energy | Replace overhead doors with insulated & motorized. | $60,783 |
| B30 Roofing – Energy | Insulation unlikely to meet code minimum. Install code minimum roof insulation. | $17,889 |
| C10 Interior Construction – Accessibility | Add accessible single use toilet. | $35,438 |
| C10 Interior Construction – Accessibility | Interior Room Signs. | $1,250 |
| D50 Electrical Systems – Energy | Replace high bay shop lighting with LED. | $21,263 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $21,263 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $11,340 |

## #9 Hokanson Gym

Use Category Educational

Area 11,880 SF

Year Constructed 1922

History/Use 1922 - Present Gymnasium & Shop Areas

Construction Type Wood Frame Structure

### DESCRIPTION

Concrete 2 story structure and basement.

Perimeter well created when basement was added after the building was built.

Houses Wood Shop and Pottery Shop on level 1.

Storage and drafting room in basement.

### Critical Needs Summary

#### SAFETY

No handrails at stair to basement.

Open riser metal stairs to access Gym.

Large openings in guardrail at perimeter well.

Metal Halide lights in Gym.

Antiquated dust collection system as a fire hazard.

#### ACCESSIBILITY

Entrance to Level one is a step up from grade.

No accessible toilet room.

Level 2 gymnasium is not accessible.

Basement level is not accessible.

#### HAZARDOUS MATERIALS

Pipe insulation.

Additional materials are suspect to have asbestos and stand in the way of ongoing maintenance.

#### DEFERRED MAINTENANCE

Clogged drain in perimeter well. Broken sump pump.

All plumbing fixtures are obsolete, worn and stained.

Aging domestic water, sanitary and storm drainage systems.

#### FIRE LIFE SAFETY/CODE

Emergency lighting maybe needed.

#### SEISMIC

Evaluation needed to confirm the extent of seismic deficiencies.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $490,965

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Accessibility | Address thresholds and replace exterior entrance doors. | $34,404 |
| B20 Exterior Enclosure – Accessibility | Replace knob style door hardware at exterior door. | $1,000 |
| C10 Interior Construction – Accessibility | Widen and replace interior doors along accessible route. | $19,987 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware at interior doors along accessible route. | $2,835 |
| C10 Interior Construction – Accessibility | Interior room signs. | $1,250 |
| C20 Stairs – Safety | Install handrails at stair to basement. | $9,639 |
| C20 Stairs – Safety | Replace railing, anti-slip tape, and add perforated metal at risers at (2) stairs up to Gym. | $45,020 |
| C20 Stairs – Safety | Replace guardrail at perimeter well. | $53,795 |
| C30 Interior Finishes – Accessibility | Add single use toilet room on level 1. | $35,438 |
| D20 Plumbing Systems – Deferred Maintenance | Piping is significantly corroded. Replace domestic water lines. | $33,680 |
| D20 Plumbing Systems – Deferred Maintenance | Address storm drainage system including clogged drain, broken downspout. | $14,175 |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital. | $126,300 |
| D50 Electrical Systems – Safety | Replace metal halide gym lighting with LED. | $21,051 |
| D50 Electrical Systems – Deferred Maintenance | Update branch circuit to sump pump. | $2,127 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit. | $3,564 |
| E10 Equipment – Safety | Replace antiquated dust collection system. | $56,700 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $2,013,919

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| A20 Basement Construction – Deferred Maintenance | Patch and repair spalling concrete and cracks. | $9,050 |
| A20 Basement Construction – Deferred Maintenance | Add vapor barrier in crawlspace. | $1,132 |
| B10 Superstructure – Seismic | Repair holes in floor. Add layer of plywood sheathing. | $268,641 |
| B10 Superstructure – Seismic | Add plywood sheathing. Reinforce sagging beams. | $26,903 |
| B10 Superstructure – Seismic | Roof to wall connections. | $49,210 |
| B20 Exterior Enclosure – Seismic | Patch cracks and add shotcrete to unreinforced concrete walls. | $916,435 |
| B20 Exterior Enclosure – General Maintenance | Clean and paint wood siding. | $1,461 |
| B30 Roofing - Deferred Maintenance (Energy) | Replace composite shingle roofing reaching life expectancy. Add code minimum roof insulation. | $175,525 |
| C30 Interior Finishes – Hazardous Materials | Abate & replace wallboard and plaster if found to contain asbestos. | $111,024 |
| C30 Interior Finishes – Seismic | Abate & replace 9x9 floor tiles with VCT. | $20,842 |
| C30 Interior Finishes – Hazardous Materials | Add plywood subfloor and install VCT. | $21,578 |
| C30 Interior Finishes – General Maintenance | Clean and paint open to structure ceiling at Gym. | $22,232 |
| D20 Plumbing Systems – Deferred Maintenance | Replace stained and obsolete plumbing fixtures. | $15,026 |
| D20 Plumbing Systems – Deferred Maintenance | Investigate clogged sanitary pipe and repair. | $9,214 |
| D30 HVAC Systems – Hazardous Materials | Replace pipe insulation. | $23,814 |
| D30 HVAC Systems – Indoor Air Quality/Ventilation | Install heating and ventilation. Add exhaust fan to kiln room. | $105,009 |
| D40 Fire Protection Systems – Fire Life Safety/Code | Replace original sprinkler system. | $130,510 |
| D50 Electrical Systems – Deferred Maintenance | Upgrade electrical service to accommodate mechanical upgrades. | $106,313 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $1,173,407

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation. | $173,453 |
| B20 Exterior Enclosure – Energy | Original single pane wood windows. Replace exterior windows. | $304,950 |
| C30 Interior Finishes – Deferred Maintenance | Replace wood gym floor. | $132,074 |
| D10 Conveying Systems – Accessibility | Add elevator to provide access to level 2 Gym and Basement. | $496,125 |
| D50 Electrical Systems – Energy | Replace inefficient lighting with LED. | $14,736 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $28,630 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $9,264 |
| E10 Equipment – Deferred Maintenance | Replace broken, worn and torn portable basketball hoops and wall padding. | $14,175 |

## #10 Paint Shop

Use Category Facilities Support

Area 1,480 SF

Year Constructed Unknown

History/Use 1940’s +/- Shop Area, Unknown Office area Addition

Construction Type Wood Frame Structure

### DESCRIPTION

One story wood frame structure.

Painted masonry exterior walls and 30 years or older tar paper shingle Roof.

Used by OSD Facilities as a Paint Shop that includes an outdated paint booth in disrepair.

### Critical Needs Summary

#### DEFERRED MAINTENANCE

As a building used only by staff, accessibility minimums do not apply.

The roof is past life expectancy and has moss.

Repair or replacement of paint booth is excluded.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $32,538

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B30 Roofing – Deferred Maintenance | Replace end of life tar paper shingle roof. | $30,693 |
| D20 Plumbing – Deferred Maintenance | Repair leaking hose bibb and unclog floor drain. | $781 |
| D20 Plumbing – Deferred Maintenance | Repair damaged and detached gutter. | $1,064 |

#### PRIORITY 1B: Long-Term Critical Needs

None

#### PRIORITY 2: Other Assessed Needs

TOTAL: $35,49

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Energy | Insulation unlikely to meet code minimum. Install code minimum roof insulation. | $8,392 |
| B20 Exterior Enclosure – Accessibility | Replace knob style door hardware at Main Entry. | $2,127 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware. | $951 |
| D50 Electrical Systems – Energy | Replace inefficient lighting with LED. | $6,294 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $12,064 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $5,666 |

## #11 Peck Gym

Use Category Educational

Area 17,752 SF

Year Constructed 1963

History/Use 1963 - Present Gymnasium and Pool, 2020 Locker Room Addition

Construction Type Concrete Piers

### DESCRIPTION

Precast concrete panels with 2x decking on glulam’s and single ply membrane Roof.

Gymnasium with full court basketball and bleachers. Performance Platform opens to the gymnasium.

Multi-lane competitive swimming Pool with observation area.

Pool equipment and abandoned locker rooms are in the basement.

Rooftop heating and ventilating units at the gym. Pool unit is heat only.

### Critical Needs Summary

#### SAFETY

Large gaps/openings at guardrails on exterior stair to basement are a safety hazard.

Main entry doors do not close properly and are often left unsecured.

Original wood bleachers missing handrails.

#### ACCESSIBILITY

Door openings along the accessible route to primary use areas are too narrow.

Door hardware repairs & upgrades needed at main entry and along accessible route.

Performance Platform is not accessible.

#### FIRE LIFE SAFETY/CODE

Emergency lighting maybe needed.

Outdated egress door hardware.

#### HAZARDOUS MATERIALS

Cracked 9x9 floor tiles exposed.

Damaged pipe insulation.

Additional materials are suspect to have asbestos and stand in the way of ongoing maintenance.

#### DEFERRED MAINTENANCE

Problematic pneumatic controls.

Aging domestic water systems.

#### INDOOR AIR QUALITY & VENTILATION

No mechanical ventilation at Pool.

#### SEISMIC

Roof to wall connections are apparent & assume plywood installed with recent roof replacement.

Evaluation needed to confirm extent of seismic deficiencies, but none included in this report.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $616,498

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Safety (Accessibility) | Replace doors at main entrance that do not close securely. | $3,000 |
| B20 Exterior Enclosure – Safety (Accessibility) | Replace door hardware at main entrance. | $1,000 |
| C10 Interior Construction – Accessibility | Interior Room Signs. | $12,426 |
| C20 Stairs – Safety | Add perforated metal infill panels at exterior guardrail at steps to basement. | $6,804 |
| C30 Interior Finishes – Hazardous Materials | Abate cracked/friable vat & replace with VCT flooring. | $10,382 |
| D20 Plumbing Systems – Accessibility | Install dual height drinking fountain. | $7,938 |
| D20 Plumbing Systems – Deferred Maintenance | Replace severely corroded domestic waterlines. | $150,982 |
| D30 HVAC Systems – Hazardous Materials | Abate and replace damaged pipe insulation. | $46,069 |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital. | $188,726 |
| D50 Electrical Systems – Safety | Replace metal halide lighting in pool with LED. | $28,940 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit. | $5,326 |
| E10 Equipment – Safety | Replace old wood bleachers missing handrail. | $154,905 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $1,178,640

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Deferred Maintenance | Investigate and repair cracks in precast wall panels. | $14,175 |
| B20 Exterior Enclosure – Fire Life Safety/Code | Replace egress hardware. | $30,257 |
| B20 Exterior Enclosure – General Maintenance | Repair crack in aluminum storefront frame. | $709 |
| B30 Roofing – General Maintenance | Investigate, patch and paint crack in plaster at skylight in locker rooms. | $639 |
| C20 Stairs – Fire Life Safety/Code | Replace handrails at pool observation deck. | $8,505 |
| C30 Interior Finishes – General Maintenance | Clean, prep, paint walls. | $69,201 |
| C30 Interior Finishes – Hazardous Materials | Abate plaster if found to contain asbestos. Add wall board and paint. | $10,771 |
| C30 Interior Finishes – General Maintenance | Refinish wood gym floor. | $120,786 |
| D20 Plumbing Systems – Deferred Maintenance | Install vacuum breaker at janitor sink faucet. | $235 |
| D20 Plumbing Systems – Deferred Maintenance | Investigate backups into Locker Room addition and repair sanitary piping. | $12,049 |
| D20 Plumbing Systems – Deferred Maintenance | Repair pool gutters. | $20,554 |
| D30 HVAC Systems – Hazardous Materials | Abate and replace duct insulation if found to contain asbestos. | $35,438 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Add heating, ventilating and humidity unit at pool. | $748,440 |
| E20 Furnishings – Deferred Maintenance | Replace gym divider curtain with broken pulley, worn and outdated. | $56, 559 |
| E20 Furnishings – Deferred Maintenance | Replace worn and outdated stage curtain and cyclorama at performance platform. | $50,322 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $267,318

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation. | $50,000 |
| B20 Exterior Enclosure – Energy | Replace inefficient exterior doors (not main entry). | $40,000 |
| B30 Roofing – Energy | Assume provided as part of recent roof replacement. | $0 |
| D50 Electrical Systems – Energy | Replace lighting with LED fixtures. | $99,396 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $50,238 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $27,682 |

## #12 Ulmer Building

Use Category Educational

Area 21,900 SF

Year Constructed 1961; 1965 Addition

History/Use 1961 - Present Classroom and Shop Building

Construction Type Concrete and Wood Frame Structure

### DESCRIPTION

One story concrete and wood frame structure.

Built-up roof.

High school classrooms and shops on central corridor.

Radiant heaters with no ventilation or cooling systems.

### Critical Needs Summary

#### ACCESSIBILITY

Staff toilet rooms are not accessible.

Classroom faucets and sinks are not accessible.

#### FIRE LIFE SAFETY/CODE

Emergency lighting may be needed.

Confirm electrical ground path meets code.

Fire sprinkler system may need to be added to meet code.

#### HAZARDOUS MATERIALS

Cracked 9x9 asbestos floor tiles exposed and under worn carpet areas.

Wall plaster and ceiling tile contains asbestos.

Asbestos exists in the attic and stands in the way of ongoing maintenance.

#### DEFERRED MAINTENANCE

Exterior doors in poor condition.

Exterior single pane windows cause heat gain in classrooms.

Problematic pneumatic controls.

All plumbing fixtures are obsolete, worn and stained.

Aging domestic water, sanitary and storm drainage systems.

Older Electrical panel & service.

#### INDOOR AIR QUALITY & VENTILATION

Radiant heaters do not provide ventilation or cooling.

Home economics cooking stoves do not have exhaust fans.

#### SEISMIC

Evaluation needed to confirm extent of seismic deficiencies.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $1,489,796

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Hazardous Materials | Abate asbestos in attic around joists. | $124,173 |
| B20 Exterior Enclosure – Deferred Maintenance | Replace all exterior wood and glass exterior doors. | $40,881 |
| B20 Exterior Enclosure – Deferred Maintenance | Paint all exposed wood fascia boards, siding, and panels. | $14,067 |
| C10 Interior Construction – Accessibility | Interior room signage. | $15,330 |
| C30 Interior Finishes – Hazardous Materials | Abate all asbestos floor tile and install new VCT. | $179,276 |
| C30 Interior Finishes – Hazardous Materials | Abate all asbestos floor tile and replace carpet in student lounge. | $15,060 |
| C30 Interior Finishes – Hazardous Materials | Abate plaster containing asbestos. Add wall board and paint. | $350,000 |
| C30 Interior Finishes – Hazardous Materials | Abate ceiling tile containing asbestos. Add ceiling tile. | $256,108 |
| C30 Interior Finishes – Accessibility | Install ceramic tile floor and wall finishes at renovated staff toilet rooms. | $21,263 |
| D20 Plumbing – Accessibility | Renovate staff toilet rooms to be accessible. Included in interior finishes above. | unknown |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital. | $232,825 |
| D40 Fire Protection – Fire Life Safety/Code | Install fire sprinkler system if determine required by current code. | $232,825 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit. | $6,570 |
| D50 Electrical Systems – Fire Life Safety/Code | Confirm and correct to make sure ground path meets code. | $1,418 |

#### PRIORITY 1B: Long-Term Critical Needs

TOTAL: $2,652,810

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B10 Superstructure – Seismic | Install roof to exterior wall connections and plywood sheathing at roof and associated costs. | $150,936 |
| B10 Superstructure – Seismic | Add additional shear walls. | $163,013 |
| B30 Roofing – Deferred Maintenance (Energy) | Replace built-up roofing system. Includes added code minimum insulation. | $1,015,809 |
| D20 Plumbing Systems – Accessibility | Replace all classroom and kitchen faucets and sinks. | $40,000 |
| D20 Plumbing Systems – Deferred Maintenance | Replace original corroded domestic waterlines. | $186,260 |

#### PRIORITY 2: Other Assessed Needs

TOTAL: $1,014,858

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation. | $151,752 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Install ventilation and cooling system (including asbestos abatement) | $1,086,514 |
| D30 HVAC Systems – Indoor Air Quality and Ventilation | Install exhaust fans at renovated staff toilet rooms and at residential cooking appliances in Home Ec room. | $10,278 |
| D50 Electrical Systems – Fire Life Safety/Code | Upgrade electrical panel, especially with HVAC upgrades. | $46,647 |
| D50 Electrical Systems – Energy | Replace inefficient lighting with LED. | $170,739 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $35,700 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $31,044 |
| E10 Equipment – Deferred Maintenance | Replace all hall lockers. | $27,897 |
| E20 Furnishings – Deferred Maintenance | Replace all cabinets in classrooms and labs. | $597,726 |

## #13 Smith Hall

Use Category: Educational

Area: 49,100 SF

Year Constructed: 1975

History/Use :1975 - Present Administration, Library, and Classroom Building

Construction Type: Wood Frame Structure

### DESCRIPTION

One story wood frame structure.

Glulam beam and cement fiber panel roof structure over central library.

Brick veneer and built-up roof.

Administration and open classroom pods with demountable partitions around central library.

Mechanical units in mechanical mezzanine provide heating with hot water from central plant and cold water from chiller.

### Critical Needs Summary

#### ACCESSIBILITY

Door hardware upgrades needed along accessible route.

Classroom faucets and sinks are not accessible.

Classroom pod kitchens are not accessible.

#### FIRE LIFE SAFETY/CODE

Emergency lighting may be needed.

Cross-corridor fire doors do not close properly.

#### HAZARDOUS MATERIALS

Asbestos flooring in some classroom pod kitchens.

#### DEFERRED MAINTENANCE

Exterior doors and windows in poor condition.

Problematic pneumatic controls.

Plumbing fixtures are obsolete, worn and stained.

Aging domestic water, sanitary and storm drainage systems.

Aging original chiller.

Older Electrical panel & service.

#### SEISMIC

Evaluation needed to confirm extent of seismic deficiencies.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $705,476

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B30 Exterior Enclosure – Deferred Maintenance | Investigate roof drains where ponding occurs and repair. | $3,402 |
| C10 Interior Construction – Accessibility | Replace knob style door hardware at interior doors along accessible route. | $30,477 |
| C10 Interior Construction – Fire Life Safety/Code | Cross-corridor doors do not close properly. Replace all cross-corridor fire doors. | $76,007 |
| C10 Interior Construction – Accessibility | Interior room signage. | $34,370 |
| C30 Interior Finishes – Hazardous Materials | Abate resilient asbestos flooring in student kitchens & replace with resilient flooring. | $22,964 |
| D20 Plumbing – Deferred Maintenance | Repair storm drain at downspout at main entry covered walkway. | $1,489 |
| D30 HVAC Systems – Deferred Maintenance | Replace problematic pneumatic controls with digital. | $522,037 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit. | $14,730 |

#### PRIORITY 1AB: Long-Term Critical Needs

TOTAL: $1,565,293

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| A10 Foundation – Seismic | Cracking at slab edge. Investigate cause and repair foundation. | $7,088 |
| B10 Superstructure – Seismic | Install roof to exterior wall connections and strengthen covered porch posts and associated costs. | $255,037 |
| B20 Exterior Enclosure – Deferred Maintenance | Replace all classroom windows. | $126,243 |
| B20 Exterior Enclosure – Deferred Maintenance | Replace all exterior doors. | $255,789 |
| B20 Exterior Enclosure – Deferred Maintenance | Investigate source of moisture penetration into brick veneer and repair. | $79,437 |
| D20 Plumbing Systems – Accessibility | Replace all classroom and kitchen faucets and sinks. | $60,599 |
| D20 Plumbing Systems – Deferred Maintenance | Replace original corroded domestic waterlines. | $348,025 |
| D30 HVAC Systems – Deferred Maintenance | Replace original chiller. | $348,025 |
| E10 Equipment – Accessibility | Replace appliances and remodel classroom pod kitchens. | $85,050 |

#### PRIORITY 2: Other Assessed Needs

TOTAL $654,482

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Energy | Insulation unlikely to meet code minimum. Install code minimum exterior wall insulation. | $140,588 |
| B20 Exterior Enclosure – Deferred Maintenance | Replace wood facias above entries & covered walkways with metal siding to reduce general maintenance. | $29,314 |
| C30 Interior Finishes – Deferred Maintenance | Replace worn carpet in west classroom pod. | $25,000 |
| C30 Interior Finishes – Deferred Maintenance | Replace all stained ceiling tiles. | $61,254 |
| C20 Stairs – Deferred Maintenance | Replace steep metal ships ladder to mechanical mezzanine with less steep ships ladder or stairs to improve access. | $14,856 |
| D50 Electrical Systems – Energy | Replace lighting with LED fixtures. | $265,140 |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $59,165 |
| D50 Electrical Systems – Energy | Add occupancy sensors. | $59,165 |

## #17 New Dormitory

Use Category: Residential

Area: 3,485 sf

Year Constructed: 2010

History/Use

- 2010: Boys Dormitory

- Present: Rec Room for Students; Rented Occasionally to the Public

Construction Type: Wood Frame Structure

### DESCRIPTION

- Constructed by “Extreme Makeover: Home Edition” and partially prefabricated off-site.

- One story wood frame structure.

- Metal roof with a green planted roof and solar panels.

- Common area with 4 dormitory rooms.

- Mechanical units in mechanical mezzanine provide heating, cooling, and ventilation for common areas.

- Unit heaters in dormitory rooms.

### Critical Needs Summary

#### SAFETY

- Lifting and cracked pavement.

- Outdated and damaged track and field equipment.

- An outdated emergency generator for the campus is located on the upper level of the Central Plant.

#### DEFERRED MAINTENANCE

- Wood siding requires frequent staining and has several holes from woodpeckers.

- Exterior metal frames around unit heaters are rusting.

#### PRIORITY 1A: Short-Term Critical Needs

TOTAL: $23,802

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| C30 Interior Finishes – Fire Life Safety/Code | Coat decorative cardboard wall finishes around dormitory beds so not combustible. | $9,072 |
| D50 Electrical Systems – Fire Life Safety/Code | Provide emergency lighting circuit. | $14,730 |

#### PRIORITY 1AB: Long-Term Critical Needs

TOTAL: $189,568

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| B20 Exterior Enclosure – Deferred Maintenance | Replace wood siding with metal siding that does not require frequent staining and is more durable. | $187,795 |
| B20 Exterior Enclosure – Deferred Maintenance | Remove rust from unit heater metal frames and paint. | $1,773 |

#### PRIORITY 2: Other Assessed Needs

TOTAL $7,412

| CATEGORY | DESCRIPTION | ESTIMATED COST |
| --- | --- | --- |
| D50 Electrical Systems – Security | Install intrusion alarm system. | $7,412 |

# Appendix 1 – Campus Roof Overview

## CARPENTER HOUSE

Type: Composition Shingle

Age: 15-20 years old

Findings: Plan to replace in next 10 years.

## WALLACE HALL

Type: Single Ply Membrane

Age: 15 years old

Findings: Plan to replace in next 10 years.

## PETERSON HALL

Type: Single ply Membrane

Age: 15 years old

Findings: Plan to replace in next 10 years.

## KUENZI HALL

Type: Composition Shingle

Age: 15 years old

Findings: Copper at Perimeter. Original roof. Active roof leaks. Replace Comp Shingles and repair Copper and transitions.

## LINDSTROM HALL

Type: Built up

Age: 12 years old

Findings: May have concealed layers of asbestos roofing. Plan to replace in next 10 years.

## TILLINGHAST BUILDING

Type: Composition Shingle

Age: 18-20 years old

Findings: Plan to replace in next 10 years.

## CLATTERBUCK BUILDING

Type: Single Ply Membrane

Age: Replaced in 2020

Findings: Standing Seam Metal perimeter Mansard Roof. Original. Good condition.

## MAINTENANCE/CENTRAL PLANT

Type: Built-up Roofing with Gravel

Age: >50 years old

Findings: Original. Several areas of ponding. End of life.

## HOKANSON GYM

Type: Composition Shingle

Age: 15-20 years old

Findings: Plan to replace in next 10 years.

## PAINT SHOP BUILDING

Type: Tar Paper Shingle

Age: 30 years old

Findings: End of life.

## PECK GYM

Type: Single Ply Membrane

Age: Replaced in 2020

Findings: New at locker room addition in 2020. Good condition.

## ULMER BUILDING

Type: Built-up Roofing

Age: 13-14 years old

Findings: Plan to replace in next 10 years.

## SMITH BUILDING

Type: Built-up Roofing

Age: Upper Roof over Library 8 years old, Lower Roof over Classrooms & Admin 5 years old

Findings: Plan to replace in next 15-20 years.

## SMITH BUILDING

Type: Built-up Roofing

Age: Upper Roof over Library 8 years old, Lower Roof over Classrooms & Admin 5 years old

Findings: Plan to replace in next 15-20 years.

## GARAGE BUILDING (NEXT TO CARPENTER HOUSE)

Type: Composition Shingle

Age: 15-20 years old

Findings: Plan to replace in next 10 years along with Carpenter House.

## CARPORT (NEXT TO TILLINGHAST BUILDING)

Type: Composition Roll

Age: Unknown

Findings: End of life.

## NEW DORMITORY BUILDING

Type: Standing Seam Metal & Green Roof

Age: New in 2011

Findings: Good condition.

# Appendix 2 – Detailed Costs from AAC

## Overview

ACC Cost Consultants, LCC

Seth J. Pszczolkowski

8060 SE Pfaffle Street, Suite 110

Tigard, OR. 97223-8489

Phone: 503.718.0075

www.archcost.com

Estimate Date: January 18, 2024

Document Date: January 03, 2024

Print Date: January 18, 2024

Print time: 1:17pm

Construction Start: To Be Determined

## DIRECT CONSTRUCTION COST SUMMARY

| Component | Area | $ /SF | Total | Replacement Cost | Replacement Cost /SF |
| --- | --- | --- | --- | --- | --- |
| Carpenter House | 1,932 sf | $311.58 | $601,979 | $469,476 | $243 |
| Wallace Hall | 7,092 sf | $287.25 | $2,037,178 | $3,350,970 | $473 |
| Peterson Hall | 24,173 sf | $252.08 | $6,093,550 | $12,727,085 | $527 |
| Kuenzi Hall | 32,904 sf | $242.13 | $7,966,985 | $16,879,752 | $513 |
| Lindstrom Hall | 55,100 sf | $281.99 | $15,537,742 | $27,522,450 | $500 |
| Tillinghast Building | 2,920 sf | $390.58 | $1,140,494 | $1,143,180 | $392 |
| Clatterbuck Building | 32,664 sf | $135.48 | $4,425,203 | $18,520,488 | $567 |
| Central Plant | 13,274 sf | $237.49 | $3,152,453 | $8,959,950 | $675 |
| Hockanson Gym | 11,880 sf | $308.35 | $3,663,223 | $5,773,680 | $486 |
| Paint Shop | 1,480 sf | $46.46 | $68,767 | $299,700 | $203 |
| Peck Gym | 17,752 sf | $116.77 | $2,072,889 | $12,941,208 | $729 |
| Ulmer Building | 21,900 sf | $218.12 | $4,776,864 | $9,608,625 | $439 |
| Smith Building | 49,104 sf | $67.71 | $3,324,907 | $22,538,736 | $459 |
| New Dormitory | 3,485 sf | $61.24 | $213,436 | $1,834,853 | $527 |
| Site Estimate | 1,300,000 sf | N/A | $8,620,489 | $87,750,000 | $68 |
| TOTAL DIRECT CONSTRUCTION COST | 1,575,660 sf | $40.43 /sf | $63,696,159 | $230,320,152 | N/Z |

The original Facility Conditions Assessment contains detailed costs for problems identified in this document. If you are interested in this detailed information, please contact OSD.